## ElectroCool Characteristics
2019.03.03
See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids / ChemFoundry, Inc.. All Rights Reserved.
Measurement Methodology |  |  |  |  | ASTM D1500 |  | ATSM D1218 | ASTM D1816 | ATM D924 | ASTM D5950 | ASTM D92 | ASTM D92 | ASTM D4052 | ASTM D1250 | ASTM D1169
Engineered Fluids Product Identifier | Engineered Fluids Product Family | Common Applications | Key Characteristics | Appearance | Color | Fluid Behavior | Refractive Index nD20 | Dielectric Strength | Dielectric Constant | Pour Point | Flash Point | Fire Point | Density (g/cc) | Coefficient of Thermal Expansion | Resistivity | Kinematic Viscosity (cSt) |  |  | Thermal Conductivity (W/m*K) |  |  | Specific Heat (J/g*K) |  |  | Heat Capacity Constant | Heat Capacity Variation | Thermal Conductivity Constant | Thermal Conductivity Variation | Coolant Recommended Operating Temperature Range (oC)
[8 empty] | kV, 2mm |  | oC | oC | oC | 16oC | volume/oC | ohm-cm | 0oC | 40oC | 100oC | 0oC | 40oC | 100oC | 0oC | 40oC | 100oC |  |  |  |  | Low | High
BC-888 | BitCool® | ASIC based Cryptocurrency mining cooling | Materially compatible with ASIC based miners | Green Tint | N/A | Non-Compressible, Isotropic, Newtonian | N/A | >40 | 2.2 | -27 | 130 | 163 | 0.82 | 0.00066 | > 1x1014 | N/A | 10 | 3.9881 | N/A | 0.1396 | 0.1373 | N/A | 2.054 | 2.2032 | 2.0577 | 0.0037833 | 0.1404 | 7.5e-05 | 5 | 100
EC-100 | ElectroCool® | General electronics cooling with excellent materials compatibility | High dielectric strength, with very good heat transfer and material compatibility | Blue Tint | N/A | Non-Compressible, Isotropic, Newtonian | N/A | >40 | 2.2 | -42 | 188 | 205 | 0.8485 | 0.00066 | > 1x1014 | 74.26 | 11.99 | 2.923 | 0.1404 | 0.1374 | 0.1329 | 2.0577 | 2.209 | 2.436 | 2.0577 | 0.0037833 | 0.1404 | 7.5e-05 | -42 | 200
EC-110 | ElectroCool® | Outdoor and sealed system electronics cooling with | Broad materials compatibility, highly stable and resistant to aging | Clear | <0.5 | Non-Compressible, Isotropic, Newtonian | 1.44 | >60 | 2.1 | -58 | 150 | 170 | 0.798 | 0.000647 | > 1x1014 | 27.4336 | 6.4 | 2 | 0.13817 | 0.1359 | 0.1325 | 2.0608 | 2.2121 | 2.439 | 2.0608 | 0.0037817 | 0.13817 | 5.6667e-05 | -58 | 165
EC-120 | ElectroCool® | Enterprise grade coolant for servers, semiconductors, and electronics | Excellent low temperature fluidity; with broad material compatibility | Clear | <0.5 | Non-Compressible, Isotropic, Newtonian | 1.442 | >60 | 2.08 | -66 | 157 | 176 | 0.798 | 0.00067 | > 1x1014 | 18.9925 | 5.0187 | 1.7033 | 0.13817 | 0.1359 | 0.1325 | 2.0608 | 2.2121 | 2.439 | 2.0608 | 0.0037817 | 0.13817 | 5.6667e-05 | -66 | 175
EC-130 | ElectroCool® | Data Center grade coolant for servers, GPUs, semiconductors, and electronics | Very low viscosity with extreme heat transfer and biodegrability | Clear | <0.5 | Non-Compressible, Isotropic, Newtonian | 1.453 | >60 | 2.2 | -60 | 135 | 155 | 0.8244 | 0.00066 | > 1x1014 | 12.1237 | 3.7248 | 1.405 | 0.1404 | 0.1374 | 0.1329 | 2.0577 | 2.209 | 2.436 | 2.0577 | 0.0037833 | 0.1404 | 7.5e-05 | -60 | 150
EC-140 | ElectroCool® | High temperature semiconductor & electronics cooling and insulation | Highly fire resistance with excellent oxidation resistance and stability | Clear | <0.5 | Non-Compressible, Isotropic, Newtonian | 1.462 | >60 | 2.22 | -54 | 280 | 304 | 0.835 | 0.000632 | > 1x1014 | 794.6096 | 66.4556 | 9.5323 | 0.16 | 0.15844 | 0.1561 | 2.046 | 2.1912 | 2.409 | 2.046 | 0.00363 | 0.16 | 3.9e-05 | -54 | 300
[8 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range | [7 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range | [7 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range | [6 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range | [6 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range | [6 empty] | Engineered Fluids Dielectric Coolant - Typical Characteristics over Operating Temperature Range
[8 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved. | [7 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved. | [7 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved. | [6 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved. | [6 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved. | [6 empty] | See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com. © 2017-2019 Engineered Fluids, LLC. All Rights Reserved.
[8 empty] | Product: | EC-100 | 7 | [5 empty] | Product: | EC-110 | 8 | [5 empty] | Product: | EC-120 | 9 |  |  |  |  | Product: | EC-120 | 9 |  |  |  |  | Product: | EC-130 | 10 |  |  |  |  | Product: | EC-140 | 11
[8 empty] | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K |  | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K |  | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K | Temp C | Kinematic Viscosity, cSt | Dynamic Viscosity, cP | Heat Capacity, KJ/Kg/K | Density, g/cc | Density, kg/m3 | Therm. Cond. W/m/K
[8 empty] | -42 | 3824.2841 | 3391.2986 | 1.8988 | 0.88678 | 886.78 | 0.14355 |  | -58 | 4456.2948 | 3998.8116 | 1.8382 | 0.89734 | 897.34 | 0.14145 |  | -66 | 6742.0379 | 6085.4983 | 1.808 | 0.90262 | 902.62 | 0.14191 | -66 | 6742.0379 | 6085.4983 | 1.808 | 0.90262 | 902.62 | 0.14191 | -60 | 891.3579 | 801.0277 | 1.8307 | 0.89866 | 898.66 | 0.1449 | -54 | 1284516.8836 | 1149257.2557 | 1.8534 | 0.8947 | 894.7 | 0.16211
[8 empty] | -41 | 3334.6511 | 2954.901 | 1.9026 | 0.88612 | 886.12 | 0.14347 |  | -57 | 3836.4818 | 3440.0965 | 1.842 | 0.89668 | 896.68 | 0.1414 |  | -65 | 5716.7786 | 5156.3056 | 1.8118 | 0.90196 | 901.96 | 0.14185 | -65 | 5716.7786 | 5156.3056 | 1.8118 | 0.90196 | 901.96 | 0.14185 | -59 | 787.0029 | 706.7286 | 1.8345 | 0.898 | 898 | 0.14483 | -53 | 1036124.2301 | 926336.5067 | 1.8572 | 0.89404 | 894.04 | 0.16207
[8 empty] | -40 | 2915.9923 | 2581.9946 | 1.9063 | 0.88546 | 885.46 | 0.1434 |  | -56 | 3313.9197 | 2969.3384 | 1.8458 | 0.89602 | 896.02 | 0.14134 |  | -64 | 4866.1355 | 4385.8479 | 1.8155 | 0.9013 | 901.3 | 0.14179 | -64 | 4866.1355 | 4385.8479 | 1.8155 | 0.9013 | 901.3 | 0.14179 | -58 | 696.8352 | 625.2981 | 1.8382 | 0.89734 | 897.34 | 0.14475 | -52 | 839311.1596 | 749823.8038 | 1.8609 | 0.89338 | 893.38 | 0.16203
[8 empty] | -39 | 2556.9785 | 2262.4145 | 1.9101 | 0.8848 | 884.8 | 0.14333 |  | -55 | 2871.8479 | 2571.3377 | 1.8496 | 0.89536 | 895.36 | 0.14128 |  | -63 | 4157.5999 | 3744.5008 | 1.8193 | 0.90064 | 900.64 | 0.14174 | -63 | 4157.5999 | 3744.5008 | 1.8193 | 0.90064 | 900.64 | 0.14174 | -57 | 618.6988 | 554.7749 | 1.842 | 0.89668 | 896.68 | 0.14467 | -51 | 682698.584 | 609458.6799 | 1.8647 | 0.89272 | 892.72 | 0.16199
[8 empty] | -38 | 2248.2385 | 1987.7575 | 1.9139 | 0.88414 | 884.14 | 0.14325 |  | -54 | 2496.6273 | 2233.7324 | 1.8534 | 0.8947 | 894.7 | 0.14123 |  | -62 | 3565.1794 | 3208.5901 | 1.8231 | 0.89998 | 899.98 | 0.14168 | -62 | 3565.1794 | 3208.5901 | 1.8231 | 0.89998 | 899.98 | 0.14168 | -56 | 550.7962 | 493.5244 | 1.8458 | 0.89602 | 896.02 | 0.1446 | -50 | 557553.8071 | 497371.4491 | 1.8685 | 0.89206 | 892.06 | 0.16195
[8 empty] | -37 | 1981.9972 | 1751.0549 | 1.9177 | 0.88348 | 883.48 | 0.14317 |  | -53 | 2177.1191 | 1946.4315 | 1.8572 | 0.89404 | 894.04 | 0.14117 |  | -61 | 3068.0064 | 2759.1195 | 1.8269 | 0.89932 | 899.32 | 0.14162 | -61 | 3068.0064 | 2759.1195 | 1.8269 | 0.89932 | 899.32 | 0.14162 | -55 | 491.6239 | 440.1804 | 1.8496 | 0.89536 | 895.36 | 0.14453 | -49 | 457145.5635 | 407499.5553 | 1.8723 | 0.8914 | 891.4 | 0.16191
[8 empty] | -36 | 1751.7843 | 1546.5102 | 1.9215 | 0.88282 | 882.82 | 0.1431 |  | -52 | 1904.1946 | 1701.1693 | 1.8609 | 0.89338 | 893.38 | 0.14111 |  | -60 | 2649.2609 | 2380.7848 | 1.8307 | 0.89866 | 898.66 | 0.14157 | -60 | 2649.2609 | 2380.7848 | 1.8307 | 0.89866 | 898.66 | 0.14157 | -54 | 439.9208 | 393.5971 | 1.8534 | 0.8947 | 894.7 | 0.14445 | -48 | 376262.9999 | 335152.5046 | 1.8761 | 0.89074 | 890.74 | 0.16187
[8 empty] | -35 | 1552.1995 | 1369.2883 | 1.9253 | 0.88216 | 882.16 | 0.14303 |  | -51 | 1670.347 | 1491.1522 | 1.8647 | 0.89272 | 892.72 | 0.14106 |  | -59 | 2295.332 | 2061.2082 | 1.8345 | 0.898 | 898 | 0.14151 | -59 | 2295.332 | 2061.2082 | 1.8345 | 0.898 | 898 | 0.14151 | -53 | 394.6256 | 352.8111 | 1.8572 | 0.89404 | 894.04 | 0.14438 | -47 | 310855.3024 | 276686.0876 | 1.8799 | 0.89008 | 890.08 | 0.16183
[8 empty] | -34 | 1378.7226 | 1215.344 | 1.929 | 0.8815 | 881.5 | 0.14295 |  | -50 | 1469.3826 | 1310.7775 | 1.8685 | 0.89206 | 892.06 | 0.141 |  | -58 | 1995.1643 | 1790.3408 | 1.8382 | 0.89734 | 897.34 | 0.14145 | -58 | 1995.1643 | 1790.3408 | 1.8382 | 0.89734 | 897.34 | 0.14145 | -52 | 354.8431 | 317.0097 | 1.8609 | 0.89338 | 893.38 | 0.1443 | -46 | 257760.5159 | 229257.358 | 1.8836 | 0.88942 | 889.42 | 0.16179
[8 empty] | -33 | 1227.5598 | 1081.2838 | 1.9328 | 0.88084 | 880.84 | 0.14288 |  | -49 | 1296.1747 | 1155.4101 | 1.8723 | 0.8914 | 891.4 | 0.14094 |  | -57 | 1739.7446 | 1559.9942 | 1.842 | 0.89668 | 896.68 | 0.1414 | -57 | 1739.7446 | 1559.9942 | 1.842 | 0.89668 | 896.68 | 0.1414 | -51 | 319.8153 | 285.5055 | 1.8647 | 0.89272 | 892.72 | 0.14422 | -45 | 214500.5965 | 190639.5502 | 1.8874 | 0.88876 | 888.76 | 0.16176
[8 empty] | -32 | 1095.5179 | 964.2529 | 1.9366 | 0.88018 | 880.18 | 0.1428 |  | -48 | 1146.466 | 1021.2031 | 1.8761 | 0.89074 | 890.74 | 0.14089 |  | -56 | 1521.698 | 1363.4719 | 1.8458 | 0.89602 | 896.02 | 0.14134 | -56 | 1521.698 | 1363.4719 | 1.8458 | 0.89602 | 896.02 | 0.14134 | -50 | 288.8994 | 257.7156 | 1.8685 | 0.89206 | 892.06 | 0.14415 | -44 | 179125.8659 | 159081.6815 | 1.8912 | 0.8881 | 888.1 | 0.16172
[8 empty] | -31 | 979.902 | 861.8434 | 1.9404 | 0.87952 | 879.52 | 0.14272 |  | -47 | 1016.7105 | 904.9536 | 1.8799 | 0.89008 | 890.08 | 0.14083 |  | -55 | 1334.9694 | 1195.2782 | 1.8496 | 0.89536 | 895.36 | 0.14128 | -55 | 1334.9694 | 1195.2782 | 1.8496 | 0.89536 | 895.36 | 0.14128 | -49 | 261.5483 | 233.1442 | 1.8723 | 0.8914 | 891.4 | 0.14408 | -43 | 150096.469 | 133201.6104 | 1.895 | 0.88744 | 887.44 | 0.16168
[8 empty] | -30 | 878.432 | 772.0188 | 1.9442 | 0.87886 | 878.86 | 0.14265 |  | -46 | 903.9456 | 803.9873 | 1.8836 | 0.88942 | 889.42 | 0.14077 |  | -54 | 1174.5695 | 1050.8874 | 1.8534 | 0.8947 | 894.7 | 0.14123 | -54 | 1174.5695 | 1050.8874 | 1.8534 | 0.8947 | 894.7 | 0.14123 | -48 | 237.2954 | 211.3685 | 1.8761 | 0.89074 | 890.74 | 0.144 | -42 | 126191.6676 | 111904.247 | 1.8988 | 0.88678 | 886.78 | 0.16164
[8 empty] | -29 | 789.174 | 693.0526 | 1.948 | 0.8782 | 878.2 | 0.14258 |  | -45 | 805.6891 | 716.0643 | 1.8874 | 0.88876 | 888.76 | 0.14072 |  | -53 | 1036.3743 | 926.5601 | 1.8572 | 0.89404 | 894.04 | 0.14117 | -53 | 1036.3743 | 926.5601 | 1.8572 | 0.89404 | 894.04 | 0.14117 | -47 | 215.7416 | 192.0273 | 1.8799 | 0.89008 | 890.08 | 0.14392 | -41 | 106440.1577 | 94318.7525 | 1.9026 | 0.88612 | 886.12 | 0.1616
[8 empty] | -28 | 710.4831 | 623.4774 | 1.9517 | 0.87754 | 877.54 | 0.1425 |  | -44 | 719.8549 | 639.3031 | 1.8912 | 0.8881 | 888.1 | 0.14066 |  | -52 | 916.9633 | 819.1967 | 1.8609 | 0.89338 | 893.38 | 0.14111 | -52 | 916.9633 | 819.1967 | 1.8609 | 0.89338 | 893.38 | 0.14111 | -46 | 196.5447 | 174.8108 | 1.8836 | 0.88942 | 889.42 | 0.14385 | -40 | 90066.3304 | 79750.1329 | 1.9063 | 0.88546 | 885.46 | 0.16156
[8 empty] | -27 | 640.9573 | 562.0426 | 1.9555 | 0.87688 | 876.88 | 0.14242 |  | -43 | 644.6851 | 572.1193 | 1.895 | 0.88744 | 887.44 | 0.1406 |  | -51 | 813.4906 | 726.2193 | 1.8647 | 0.89272 | 892.72 | 0.14106 | -51 | 813.4906 | 726.2193 | 1.8647 | 0.89272 | 892.72 | 0.14106 | -45 | 179.4106 | 159.4529 | 1.8874 | 0.88876 | 888.76 | 0.14377 | -39 | 76448.6711 | 67641.7842 | 1.9101 | 0.8848 | 884.8 | 0.16152
[8 empty] | -26 | 579.3984 | 507.6804 | 1.9593 | 0.87622 | 876.22 | 0.14235 |  | -42 | 578.6943 | 513.1745 | 1.8988 | 0.88678 | 886.78 | 0.14055 |  | -50 | 723.5813 | 645.4779 | 1.8685 | 0.89206 | 892.06 | 0.141 | -50 | 723.5813 | 645.4779 | 1.8685 | 0.89206 | 892.06 | 0.141 | -44 | 164.0858 | 145.7246 | 1.8912 | 0.8881 | 888.1 | 0.1437 | -38 | 65087.4356 | 57546.4053 | 1.9139 | 0.88414 | 884.14 | 0.16148
[8 empty] | -25 | 524.7801 | 459.4765 | 1.9631 | 0.87556 | 875.56 | 0.14227 |  | -41 | 520.6239 | 461.3353 | 1.9026 | 0.88612 | 886.12 | 0.14049 |  | -49 | 645.2472 | 575.1734 | 1.8723 | 0.8914 | 891.4 | 0.14094 | -49 | 645.2472 | 575.1734 | 1.8723 | 0.8914 | 891.4 | 0.14094 | -43 | 150.3517 | 133.4281 | 1.895 | 0.88744 | 887.44 | 0.14363 | -37 | 55579.4432 | 49103.3265 | 1.9177 | 0.88348 | 883.48 | 0.16144
[8 empty] | -24 | 476.2217 | 416.6464 | 1.9669 | 0.8749 | 874.9 | 0.1422 |  | -40 | 469.4049 | 415.6393 | 1.9063 | 0.88546 | 885.46 | 0.14043 |  | -48 | 576.8191 | 513.7958 | 1.8761 | 0.89074 | 890.74 | 0.14089 | -48 | 576.8191 | 513.7958 | 1.8761 | 0.89074 | 890.74 | 0.14089 | -42 | 138.0189 | 122.3924 | 1.8988 | 0.88678 | 886.78 | 0.14355 | -36 | 47598.3496 | 42020.775 | 1.9215 | 0.88282 | 882.82 | 0.1614
[8 empty] | -23 | 432.965 | 378.5153 | 1.9707 | 0.87424 | 874.24 | 0.14213 |  | -39 | 424.1267 | 375.2673 | 1.9101 | 0.8848 | 884.8 | 0.14038 |  | -47 | 516.8916 | 460.0749 | 1.8799 | 0.89008 | 890.08 | 0.14083 | -47 | 516.8916 | 460.0749 | 1.8799 | 0.89008 | 890.08 | 0.14083 | -41 | 126.923 | 112.469 | 1.9026 | 0.88612 | 886.12 | 0.14347 | -35 | 40879.1546 | 36061.955 | 1.9253 | 0.88216 | 882.16 | 0.16137
[8 empty] | -22 | 394.3565 | 344.502 | 1.9744 | 0.87358 | 873.58 | 0.14205 |  | -38 | 384.0119 | 339.5202 | 1.9139 | 0.88414 | 884.14 | 0.14032 |  | -46 | 464.2779 | 412.938 | 1.8836 | 0.88942 | 889.42 | 0.14077 | -46 | 464.2779 | 412.938 | 1.8836 | 0.88942 | 889.42 | 0.14077 | -40 | 116.9213 | 103.5291 | 1.9063 | 0.88546 | 885.46 | 0.1434 | -34 | 35205.9942 | 31034.0839 | 1.929 | 0.8815 | 881.5 | 0.16133
[8 empty] | -21 | 359.8315 | 314.1041 | 1.9782 | 0.87292 | 872.92 | 0.14197 |  | -37 | 348.3951 | 307.8001 | 1.9177 | 0.88348 | 883.48 | 0.14026 |  | -45 | 417.9733 | 371.478 | 1.8874 | 0.88876 | 888.76 | 0.14072 | -45 | 417.9733 | 371.478 | 1.8874 | 0.88876 | 888.76 | 0.14072 | -39 | 107.8894 | 95.4605 | 1.9101 | 0.8848 | 884.8 | 0.14333 | -33 | 30402.4886 | 26779.7281 | 1.9328 | 0.88084 | 880.84 | 0.16129
[8 empty] | -20 | 328.9007 | 286.8869 | 1.982 | 0.87226 | 872.26 | 0.1419 |  | -36 | 316.7055 | 279.5939 | 1.9215 | 0.88282 | 882.82 | 0.14021 |  | -44 | 377.1248 | 334.9246 | 1.8912 | 0.8881 | 888.1 | 0.14066 | -44 | 377.1248 | 334.9246 | 1.8912 | 0.8881 | 888.1 | 0.14066 | -38 | 99.7186 | 88.1652 | 1.9139 | 0.88414 | 884.14 | 0.14325 | -32 | 26324.0854 | 23169.9335 | 1.9366 | 0.88018 | 880.18 | 0.16125
[8 empty] | -19 | 301.1399 | 262.4736 | 1.9858 | 0.8716 | 871.6 | 0.14183 |  | -35 | 288.4522 | 254.461 | 1.9253 | 0.88216 | 882.16 | 0.14015 |  | -43 | 341.0064 | 302.6227 | 1.895 | 0.88744 | 887.44 | 0.1406 | -43 | 341.0064 | 302.6227 | 1.895 | 0.88744 | 887.44 | 0.1406 | -37 | 92.3141 | 81.5577 | 1.9177 | 0.88348 | 883.48 | 0.14317 | -31 | 22851.967 | 20098.7621 | 1.9404 | 0.87952 | 879.52 | 0.16121
[8 empty] | -18 | 276.1801 | 240.5363 | 1.9896 | 0.87094 | 870.94 | 0.14175 |  | -34 | 263.2121 | 232.0215 | 1.929 | 0.8815 | 881.5 | 0.14009 |  | -42 | 308.9984 | 274.0136 | 1.8988 | 0.88678 | 886.78 | 0.14055 | -42 | 308.9984 | 274.0136 | 1.8988 | 0.88678 | 886.78 | 0.14055 | -36 | 85.5926 | 75.5628 | 1.9215 | 0.88282 | 882.82 | 0.1431 | -30 | 19888.1872 | 17478.9322 | 1.9442 | 0.87886 | 878.86 | 0.16117
[8 empty] | -17 | 253.6998 | 220.7899 | 1.9934 | 0.87028 | 870.28 | 0.14167 |  | -33 | 240.6199 | 211.9476 | 1.9328 | 0.88084 | 880.84 | 0.14004 |  | -41 | 280.5708 | 248.6194 | 1.9026 | 0.88612 | 886.12 | 0.14049 | -41 | 280.5708 | 248.6194 | 1.9026 | 0.88612 | 886.12 | 0.14049 | -35 | 79.4808 | 70.1148 | 1.9253 | 0.88216 | 882.16 | 0.14303 | -29 | 17351.7762 | 15238.3298 | 1.948 | 0.8782 | 878.2 | 0.16113
[8 empty] | -16 | 233.4184 | 202.9853 | 1.9971 | 0.86962 | 869.62 | 0.1416 |  | -32 | 220.3591 | 193.9557 | 1.9366 | 0.88018 | 880.18 | 0.13998 |  | -40 | 255.2691 | 226.0305 | 1.9063 | 0.88546 | 885.46 | 0.14043 | -40 | 255.2691 | 226.0305 | 1.9063 | 0.88546 | 885.46 | 0.14043 | -34 | 73.9146 | 65.1557 | 1.929 | 0.8815 | 881.5 | 0.14295 | -28 | 15175.6128 | 13317.2072 | 1.9517 | 0.87754 | 877.54 | 0.16109
[8 empty] | -15 | 215.0906 | 186.9051 | 2.0009 | 0.86896 | 868.96 | 0.14153 |  | -31 | 202.1553 | 177.7996 | 1.9404 | 0.87952 | 879.52 | 0.13992 |  | -39 | 232.7025 | 205.8951 | 1.9101 | 0.8848 | 884.8 | 0.14038 | -39 | 232.7025 | 205.8951 | 1.9101 | 0.8848 | 884.8 | 0.14038 | -33 | 68.8372 | 60.6346 | 1.9328 | 0.88084 | 880.84 | 0.14288 | -27 | 13303.9053 | 11665.9284 | 1.9555 | 0.87688 | 876.88 | 0.16105
[8 empty] | -14 | 198.5014 | 172.3587 | 2.0047 | 0.8683 | 868.3 | 0.14145 |  | -30 | 185.7698 | 163.2656 | 1.9442 | 0.87886 | 878.86 | 0.13987 |  | -38 | 212.5343 | 187.9101 | 1.9139 | 0.88414 | 884.14 | 0.14032 | -38 | 212.5343 | 187.9101 | 1.9139 | 0.88414 | 884.14 | 0.14032 | -32 | 64.1985 | 56.5063 | 1.9366 | 0.88018 | 880.18 | 0.1428 | -26 | 11690.1555 | 10243.148 | 1.9593 | 0.87622 | 876.22 | 0.16101
[8 empty] | -13 | 183.462 | 159.1789 | 2.0085 | 0.86764 | 867.64 | 0.14138 |  | -29 | 170.9948 | 150.1676 | 1.948 | 0.8782 | 878.2 | 0.13981 |  | -37 | 194.4739 | 171.8138 | 1.9177 | 0.88348 | 883.48 | 0.14026 | -37 | 194.4739 | 171.8138 | 1.9177 | 0.88348 | 883.48 | 0.14026 | -31 | 59.9543 | 52.731 | 1.9404 | 0.87952 | 879.52 | 0.14272 | -25 | 10295.51 | 9014.3368 | 1.9631 | 0.87556 | 875.56 | 0.16098
[8 empty] | -12 | 169.8065 | 147.2189 | 2.0123 | 0.86698 | 866.98 | 0.1413 |  | -28 | 157.6488 | 138.3432 | 1.9517 | 0.87754 | 877.54 | 0.13975 |  | -36 | 178.2695 | 157.3799 | 1.9215 | 0.88282 | 882.82 | 0.14021 | -36 | 178.2695 | 157.3799 | 1.9215 | 0.88282 | 882.82 | 0.14021 | -30 | 56.0652 | 49.2735 | 1.9442 | 0.87886 | 878.86 | 0.14265 | -24 | 9087.4207 | 7950.5844 | 1.9669 | 0.8749 | 874.9 | 0.16094
[8 empty] | -11 | 157.3889 | 136.3491 | 2.0161 | 0.86632 | 866.32 | 0.14122 |  | -27 | 145.5733 | 127.6503 | 1.9555 | 0.87688 | 876.88 | 0.1397 |  | -35 | 163.7029 | 144.4121 | 1.9253 | 0.88216 | 882.16 | 0.14015 | -35 | 163.7029 | 144.4121 | 1.9253 | 0.88216 | 882.16 | 0.14015 | -29 | 52.4965 | 46.1024 | 1.948 | 0.8782 | 878.2 | 0.14258 | -23 | 8038.553 | 7027.6246 | 1.9707 | 0.87424 | 874.24 | 0.1609
[8 empty] | -10 | 146.0801 | 126.4557 | 2.0198 | 0.86566 | 865.66 | 0.14115 |  | -26 | 134.629 | 117.9647 | 1.9593 | 0.87622 | 876.22 | 0.13964 |  | -34 | 150.5844 | 132.7401 | 1.929 | 0.8815 | 881.5 | 0.14009 | -34 | 150.5844 | 132.7401 | 1.929 | 0.8815 | 881.5 | 0.14009 | -28 | 49.2171 | 43.19 | 1.9517 | 0.87754 | 877.54 | 0.1425 | -22 | 7125.8949 | 6225.0393 | 1.9744 | 0.87358 | 873.58 | 0.16086
[8 empty] | -9 | 135.7662 | 117.4378 | 2.0236 | 0.865 | 865 | 0.14108 |  | -25 | 124.6941 | 109.1772 | 1.9631 | 0.87556 | 875.56 | 0.13958 |  | -33 | 138.7487 | 122.2154 | 1.9328 | 0.88084 | 880.84 | 0.14004 | -33 | 138.7487 | 122.2154 | 1.9328 | 0.88084 | 880.84 | 0.14004 | -27 | 46.1995 | 40.5114 | 1.9555 | 0.87688 | 876.88 | 0.14242 | -21 | 6330.0267 | 5525.6069 | 1.9782 | 0.87292 | 872.92 | 0.16082
[8 empty] | -8 | 126.3463 | 109.2062 | 2.0274 | 0.86434 | 864.34 | 0.141 |  | -24 | 115.6611 | 101.1919 | 1.9669 | 0.8749 | 874.9 | 0.13953 |  | -32 | 128.0515 | 112.7084 | 1.9366 | 0.88018 | 880.18 | 0.13998 | -32 | 128.0515 | 112.7084 | 1.9366 | 0.88018 | 880.18 | 0.13998 | -26 | 43.419 | 38.0446 | 1.9593 | 0.87622 | 876.22 | 0.14235 | -20 | 5634.522 | 4914.7682 | 1.982 | 0.87226 | 872.26 | 0.16078
[8 empty] | -7 | 117.731 | 101.6819 | 2.0312 | 0.86368 | 863.68 | 0.14092 |  | -23 | 107.4354 | 93.9243 | 1.9707 | 0.87424 | 874.24 | 0.13947 |  | -31 | 118.3668 | 104.1059 | 1.9404 | 0.87952 | 879.52 | 0.13992 | -31 | 118.3668 | 104.1059 | 1.9404 | 0.87952 | 879.52 | 0.13992 | -25 | 40.8537 | 35.7699 | 1.9631 | 0.87556 | 875.56 | 0.14227 | -19 | 5025.454 | 4380.1857 | 1.9858 | 0.8716 | 871.6 | 0.16074
[8 empty] | -6 | 109.8408 | 94.7948 | 2.035 | 0.86302 | 863.02 | 0.14085 |  | -22 | 99.9336 | 87.3 | 1.9744 | 0.87358 | 873.58 | 0.13941 |  | -30 | 109.5839 | 96.3089 | 1.9442 | 0.87886 | 878.86 | 0.13987 | -30 | 109.5839 | 96.3089 | 1.9442 | 0.87886 | 878.86 | 0.13987 | -24 | 38.4839 | 33.6696 | 1.9669 | 0.8749 | 874.9 | 0.1422 | -18 | 4490.9887 | 3911.3817 | 1.9896 | 0.87094 | 870.94 | 0.1607
[8 empty] | -5 | 102.6051 | 88.4825 | 2.0388 | 0.86236 | 862.36 | 0.14077 |  | -21 | 93.0818 | 81.253 | 1.9782 | 0.87292 | 872.92 | 0.13936 |  | -29 | 101.6058 | 89.2303 | 1.948 | 0.8782 | 878.2 | 0.13981 | -29 | 101.6058 | 89.2303 | 1.948 | 0.8782 | 878.2 | 0.13981 | -23 | 36.2919 | 31.7278 | 1.9707 | 0.87424 | 874.24 | 0.14213 | -17 | 4021.0478 | 3499.4374 | 1.9934 | 0.87028 | 870.28 | 0.16066
[8 empty] | -4 | 95.9609 | 82.6895 | 2.0425 | 0.8617 | 861.7 | 0.1407 |  | -20 | 86.8147 | 75.725 | 1.982 | 0.87226 | 872.26 | 0.1393 |  | -28 | 94.3473 | 82.7935 | 1.9517 | 0.87754 | 877.54 | 0.13975 | -28 | 94.3473 | 82.7935 | 1.9517 | 0.87754 | 877.54 | 0.13975 | -22 | 34.262 | 29.9306 | 1.9744 | 0.87358 | 873.58 | 0.14205 | -16 | 3607.03 | 3136.7454 | 1.9971 | 0.86962 | 869.62 | 0.16062
[8 empty] | -3 | 89.8522 | 77.3663 | 2.0463 | 0.86104 | 861.04 | 0.14062 |  | -19 | 81.0742 | 70.6643 | 1.9858 | 0.8716 | 871.6 | 0.13924 |  | -27 | 87.7329 | 76.9313 | 1.9555 | 0.87688 | 876.88 | 0.1397 | -27 | 87.7329 | 76.9313 | 1.9555 | 0.87688 | 876.88 | 0.1397 | -21 | 32.3798 | 28.265 | 1.9782 | 0.87292 | 872.92 | 0.14197 | -15 | 3241.5787 | 2816.8023 | 2.0009 | 0.86896 | 868.96 | 0.16059
[8 empty] | -2 | 84.2286 | 72.4686 | 2.0501 | 0.86038 | 860.38 | 0.14055 |  | -18 | 75.8089 | 66.025 | 1.9896 | 0.87094 | 870.94 | 0.13919 |  | -26 | 81.6965 | 71.5841 | 1.9593 | 0.87622 | 876.22 | 0.13964 | -26 | 81.6965 | 71.5841 | 1.9593 | 0.87622 | 876.22 | 0.13964 | -20 | 30.6327 | 26.7197 | 1.982 | 0.87226 | 872.26 | 0.1419 | -14 | 2918.3889 | 2534.0371 | 2.0047 | 0.8683 | 868.3 | 0.16055
[8 empty] | -1 | 79.0455 | 67.957 | 2.0539 | 0.85972 | 859.72 | 0.14047 |  | -17 | 70.9729 | 61.7663 | 1.9934 | 0.87028 | 870.28 | 0.13913 |  | -25 | 76.1791 | 66.6994 | 1.9631 | 0.87556 | 875.56 | 0.13958 | -25 | 76.1791 | 66.6994 | 1.9631 | 0.87556 | 875.56 | 0.13958 | -19 | 29.009 | 25.2842 | 1.9858 | 0.8716 | 871.6 | 0.14183 | -13 | 2632.0454 | 2283.6678 | 2.0085 | 0.86764 | 867.64 | 0.16051
[8 empty] | 0 | 74.2624 | 63.7959 | 2.0577 | 0.85906 | 859.06 | 0.1404 |  | -16 | 66.5253 | 57.8518 | 1.9971 | 0.86962 | 869.62 | 0.13907 |  | -24 | 71.129 | 62.2307 | 1.9669 | 0.8749 | 874.9 | 0.13953 | -24 | 71.129 | 62.2307 | 1.9669 | 0.8749 | 874.9 | 0.13953 | -18 | 27.4984 | 23.9494 | 1.9896 | 0.87094 | 870.94 | 0.14175 | -12 | 2377.8883 | 2061.5816 | 2.0123 | 0.86698 | 866.98 | 0.16047
[8 empty] | 1 | 69.8435 | 59.9536 | 2.0615 | 0.8584 | 858.4 | 0.14033 |  | -15 | 62.4297 | 54.2489 | 2.0009 | 0.86896 | 868.96 | 0.13902 |  | -23 | 66.4998 | 58.1368 | 1.9707 | 0.87424 | 874.24 | 0.13947 | -23 | 66.4998 | 58.1368 | 1.9707 | 0.87424 | 874.24 | 0.13947 | -17 | 26.0914 | 22.7068 | 1.9934 | 0.87028 | 870.28 | 0.14167 | -11 | 2151.8998 | 1864.2338 | 2.0161 | 0.86632 | 866.32 | 0.16043
[8 empty] | 2 | 65.7562 | 56.4017 | 2.0652 | 0.85774 | 857.74 | 0.14025 |  | -14 | 58.6533 | 50.9287 | 2.0047 | 0.8683 | 868.3 | 0.13896 |  | -22 | 62.2506 | 54.3809 | 1.9744 | 0.87358 | 873.58 | 0.13941 | -22 | 62.2506 | 54.3809 | 1.9744 | 0.87358 | 873.58 | 0.13941 | -16 | 24.7796 | 21.5488 | 1.9971 | 0.86962 | 869.62 | 0.1416 | -10 | 1950.6086 | 1688.5638 | 2.0198 | 0.86566 | 865.66 | 0.16039
[8 empty] | 3 | 61.9714 | 53.1145 | 2.069 | 0.85708 | 857.08 | 0.14017 |  | -13 | 55.1671 | 47.8652 | 2.0085 | 0.86764 | 867.64 | 0.1389 |  | -21 | 58.3449 | 50.9304 | 1.9782 | 0.87292 | 872.92 | 0.13936 | -21 | 58.3449 | 50.9304 | 1.9782 | 0.87292 | 872.92 | 0.13936 | -15 | 23.5552 | 20.4685 | 2.0009 | 0.86896 | 868.96 | 0.14153 | -9 | 1771.0102 | 1531.9238 | 2.0236 | 0.865 | 865 | 0.16035
[8 empty] | 4 | 58.463 | 50.0688 | 2.0728 | 0.85642 | 856.42 | 0.1401 |  | -12 | 51.9448 | 45.0351 | 2.0123 | 0.86698 | 866.98 | 0.13885 |  | -20 | 54.7501 | 47.7563 | 1.982 | 0.87226 | 872.26 | 0.1393 | -20 | 54.7501 | 47.7563 | 1.982 | 0.87226 | 872.26 | 0.1393 | -14 | 22.4113 | 19.4597 | 2.0047 | 0.8683 | 868.3 | 0.14145 | -8 | 1610.4993 | 1392.0189 | 2.0274 | 0.86434 | 864.34 | 0.16031
[8 empty] | 5 | 55.2071 | 47.244 | 2.0766 | 0.85576 | 855.76 | 0.14003 |  | -11 | 48.963 | 42.4176 | 2.0161 | 0.86632 | 866.32 | 0.13879 |  | -19 | 51.4372 | 44.8327 | 1.9858 | 0.8716 | 871.6 | 0.13924 | -19 | 51.4372 | 44.8327 | 1.9858 | 0.8716 | 871.6 | 0.13924 | -13 | 21.3414 | 18.5166 | 2.0085 | 0.86764 | 867.64 | 0.14138 | -7 | 1466.8124 | 1266.8566 | 2.0312 | 0.86368 | 863.68 | 0.16027
[8 empty] | 6 | 52.1824 | 44.6211 | 2.0804 | 0.8551 | 855.1 | 0.13995 |  | -10 | 46.2004 | 39.9938 | 2.0198 | 0.86566 | 865.66 | 0.13873 |  | -18 | 48.3802 | 42.1362 | 1.9896 | 0.87094 | 870.94 | 0.13919 | -18 | 48.3802 | 42.1362 | 1.9896 | 0.87094 | 870.94 | 0.13919 | -12 | 20.3398 | 17.6342 | 2.0123 | 0.86698 | 866.98 | 0.1413 | -6 | 1337.9799 | 1154.7034 | 2.035 | 0.86302 | 863.02 | 0.16023
[8 empty] | 7 | 49.3695 | 42.1833 | 2.0842 | 0.85444 | 854.44 | 0.13987 |  | -9 | 43.6381 | 37.7469 | 2.0236 | 0.865 | 865 | 0.13868 |  | -17 | 45.5558 | 39.6463 | 1.9934 | 0.87028 | 870.28 | 0.13913 | -17 | 45.5558 | 39.6463 | 1.9934 | 0.87028 | 870.28 | 0.13913 | -11 | 19.4013 | 16.8078 | 2.0161 | 0.86632 | 866.32 | 0.14122 | -5 | 1222.2842 | 1054.049 | 2.0388 | 0.86236 | 862.36 | 0.1602
[8 empty] | 8 | 46.7511 | 39.9151 | 2.0879 | 0.85378 | 853.78 | 0.1398 |  | -8 | 41.2588 | 35.6617 | 2.0274 | 0.86434 | 864.34 | 0.13862 |  | -16 | 42.9431 | 37.3442 | 1.9971 | 0.86962 | 869.62 | 0.13907 | -16 | 42.9431 | 37.3442 | 1.9971 | 0.86962 | 869.62 | 0.13907 | -10 | 18.5211 | 16.033 | 2.0198 | 0.86566 | 865.66 | 0.14115 | -4 | 1118.2256 | 963.575 | 2.0425 | 0.8617 | 861.7 | 0.16016
[8 empty] | 9 | 44.3111 | 37.8027 | 2.0917 | 0.85312 | 853.12 | 0.13972 |  | -7 | 39.0472 | 33.7243 | 2.0312 | 0.86368 | 863.68 | 0.13856 |  | -15 | 40.5234 | 35.2132 | 2.0009 | 0.86896 | 868.96 | 0.13902 | -15 | 40.5234 | 35.2132 | 2.0009 | 0.86896 | 868.96 | 0.13902 | -9 | 17.6947 | 15.3059 | 2.0236 | 0.865 | 865 | 0.14108 | -3 | 1024.4919 | 882.1285 | 2.0463 | 0.86104 | 861.04 | 0.16012
[8 empty] | 10 | 42.0353 | 35.8334 | 2.0955 | 0.85246 | 852.46 | 0.13965 |  | -6 | 36.9892 | 31.9224 | 2.035 | 0.86302 | 863.02 | 0.13851 |  | -14 | 38.2798 | 33.2384 | 2.0047 | 0.8683 | 868.3 | 0.13896 | -14 | 38.2798 | 33.2384 | 2.0047 | 0.8683 | 868.3 | 0.13896 | -8 | 16.9183 | 14.6231 | 2.0274 | 0.86434 | 864.34 | 0.141 | -2 | 939.9335 | 808.7 | 2.0501 | 0.86038 | 860.38 | 0.16008
[8 empty] | 11 | 39.9105 | 33.9958 | 2.0993 | 0.8518 | 851.8 | 0.13958 |  | -5 | 35.0721 | 30.2448 | 2.0388 | 0.86236 | 862.36 | 0.13845 |  | -13 | 36.1972 | 31.4061 | 2.0085 | 0.86764 | 867.64 | 0.1389 | -13 | 36.1972 | 31.4061 | 2.0085 | 0.86764 | 867.64 | 0.1389 | -7 | 16.188 | 13.9813 | 2.0312 | 0.86368 | 863.68 | 0.14092 | -1 | 863.5413 | 742.4037 | 2.0539 | 0.85972 | 859.72 | 0.16004
[8 empty] | 12 | 37.9249 | 32.2794 | 2.1031 | 0.85114 | 851.14 | 0.1395 |  | -4 | 33.2846 | 28.6813 | 2.0425 | 0.8617 | 861.7 | 0.13839 |  | -12 | 34.2618 | 29.7043 | 2.0123 | 0.86698 | 866.98 | 0.13885 | -12 | 34.2618 | 29.7043 | 2.0123 | 0.86698 | 866.98 | 0.13885 | -6 | 15.5007 | 13.3774 | 2.035 | 0.86302 | 863.02 | 0.14085 | 0 | 794.4281 | 682.4614 | 2.0577 | 0.85906 | 859.06 | 0.16
[8 empty] | 13 | 36.0676 | 30.6748 | 2.1069 | 0.85048 | 850.48 | 0.13942 |  | -3 | 31.6161 | 27.2227 | 2.0463 | 0.86104 | 861.04 | 0.13834 |  | -11 | 32.4612 | 28.1218 | 2.0161 | 0.86632 | 866.32 | 0.13879 | -11 | 32.4612 | 28.1218 | 2.0161 | 0.86632 | 866.32 | 0.13879 | -5 | 14.8532 | 12.8088 | 2.0388 | 0.86236 | 862.36 | 0.14077 | 1 | 731.8127 | 628.1881 | 2.0615 | 0.8584 | 858.4 | 0.15996
[8 empty] | 14 | 34.3288 | 29.1733 | 2.1106 | 0.84982 | 849.82 | 0.13935 |  | -2 | 30.0572 | 25.8606 | 2.0501 | 0.86038 | 860.38 | 0.13828 |  | -10 | 30.7844 | 26.6488 | 2.0198 | 0.86566 | 865.66 | 0.13873 | -10 | 30.7844 | 26.6488 | 2.0198 | 0.86566 | 865.66 | 0.13873 | -4 | 14.2427 | 12.2729 | 2.0425 | 0.8617 | 861.7 | 0.1407 | 2 | 675.0065 | 578.9801 | 2.0652 | 0.85774 | 857.74 | 0.15992
[8 empty] | 15 | 32.6995 | 27.7671 | 2.1144 | 0.84916 | 849.16 | 0.13927 |  | -1 | 28.5993 | 24.5874 | 2.0539 | 0.85972 | 859.72 | 0.13822 |  | -9 | 29.221 | 25.2762 | 2.0236 | 0.865 | 865 | 0.13868 | -9 | 29.221 | 25.2762 | 2.0236 | 0.865 | 865 | 0.13868 | -3 | 13.6667 | 11.7675 | 2.0463 | 0.86104 | 861.04 | 0.14062 | 3 | 623.401 | 534.3045 | 2.069 | 0.85708 | 857.08 | 0.15988
[8 empty] | 16 | 31.1714 | 26.4489 | 2.1182 | 0.8485 | 848.5 | 0.1392 |  | 0 | 27.2346 | 23.3961 | 2.0577 | 0.85906 | 859.06 | 0.13817 |  | -8 | 27.7621 | 23.9959 | 2.0274 | 0.86434 | 864.34 | 0.13862 | -8 | 27.7621 | 23.9959 | 2.0274 | 0.86434 | 864.34 | 0.13862 | -2 | 13.1227 | 11.2905 | 2.0501 | 0.86038 | 860.38 | 0.14055 | 4 | 576.4581 | 493.6902 | 2.0728 | 0.85642 | 856.42 | 0.15984
[8 empty] | 17 | 29.7371 | 25.2123 | 2.122 | 0.84784 | 847.84 | 0.13912 |  | 1 | 25.956 | 22.2806 | 2.0615 | 0.8584 | 858.4 | 0.13811 |  | -7 | 26.3992 | 22.8004 | 2.0312 | 0.86368 | 863.68 | 0.13856 | -7 | 26.3992 | 22.8004 | 2.0312 | 0.86368 | 863.68 | 0.13856 | -1 | 12.6086 | 10.8398 | 2.0539 | 0.85972 | 859.72 | 0.14047 | 5 | 533.7011 | 456.7201 | 2.0766 | 0.85576 | 855.76 | 0.15981
[8 empty] | 18 | 28.3897 | 24.0512 | 2.1258 | 0.84718 | 847.18 | 0.13905 |  | 2 | 24.7569 | 21.235 | 2.0652 | 0.85774 | 857.74 | 0.13805 |  | -6 | 25.1247 | 21.6831 | 2.035 | 0.86302 | 863.02 | 0.13851 | -6 | 25.1247 | 21.6831 | 2.035 | 0.86302 | 863.02 | 0.13851 | 0 | 12.1224 | 10.4138 | 2.0577 | 0.85906 | 859.06 | 0.1404 | 6 | 494.7073 | 423.0242 | 2.0804 | 0.8551 | 855.1 | 0.15977
[8 empty] | 19 | 27.1228 | 22.96 | 2.1296 | 0.84652 | 846.52 | 0.13897 |  | 3 | 23.6314 | 20.254 | 2.069 | 0.85708 | 857.08 | 0.138 |  | -5 | 23.9319 | 20.6379 | 2.0388 | 0.86236 | 862.36 | 0.13845 | -5 | 23.9319 | 20.6379 | 2.0388 | 0.86236 | 862.36 | 0.13845 | 1 | 11.6622 | 10.0108 | 2.0615 | 0.8584 | 858.4 | 0.14033 | 7 | 459.101 | 392.2742 | 2.0842 | 0.85444 | 854.44 | 0.15973
[8 empty] | 20 | 25.9307 | 21.9338 | 2.1333 | 0.84586 | 845.86 | 0.1389 |  | 4 | 22.5741 | 19.3329 | 2.0728 | 0.85642 | 856.42 | 0.13794 |  | -4 | 22.8143 | 19.6591 | 2.0425 | 0.8617 | 861.7 | 0.13839 | -4 | 22.8143 | 19.6591 | 2.0425 | 0.8617 | 861.7 | 0.13839 | 2 | 11.2263 | 9.6292 | 2.0652 | 0.85774 | 857.74 | 0.14025 | 8 | 426.548 | 364.1782 | 2.0879 | 0.85378 | 853.78 | 0.15969
[8 empty] | 21 | 24.8082 | 20.9679 | 2.1371 | 0.8452 | 845.2 | 0.13883 |  | 5 | 21.58 | 18.4673 | 2.0766 | 0.85576 | 855.76 | 0.13788 |  | -3 | 21.7664 | 18.7417 | 2.0463 | 0.86104 | 861.04 | 0.13834 | -3 | 21.7664 | 18.7417 | 2.0463 | 0.86104 | 861.04 | 0.13834 | 3 | 10.8131 | 9.2677 | 2.069 | 0.85708 | 857.08 | 0.14017 | 9 | 396.7508 | 338.4761 | 2.0917 | 0.85312 | 853.12 | 0.15965
[8 empty] | 22 | 23.7503 | 20.058 | 2.1409 | 0.84454 | 844.54 | 0.13875 |  | 6 | 20.6446 | 17.6532 | 2.0804 | 0.8551 | 855.1 | 0.13783 |  | -2 | 20.7828 | 17.8811 | 2.0501 | 0.86038 | 860.38 | 0.13828 | -2 | 20.7828 | 17.8811 | 2.0501 | 0.86038 | 860.38 | 0.13828 | 4 | 10.4213 | 8.925 | 2.0728 | 0.85642 | 856.42 | 0.1401 | 10 | 369.4439 | 314.9361 | 2.0955 | 0.85246 | 852.46 | 0.15961
[8 empty] | 23 | 22.7525 | 19.2004 | 2.1447 | 0.84388 | 843.88 | 0.13867 |  | 7 | 19.7636 | 16.8868 | 2.0842 | 0.85444 | 854.44 | 0.13777 |  | -1 | 19.8589 | 17.0731 | 2.0539 | 0.85972 | 859.72 | 0.13822 | -1 | 19.8589 | 17.0731 | 2.0539 | 0.85972 | 859.72 | 0.13822 | 5 | 10.0493 | 8.5998 | 2.0766 | 0.85576 | 855.76 | 0.14003 | 11 | 344.39 | 293.3514 | 2.0993 | 0.8518 | 851.8 | 0.15957
[8 empty] | 24 | 21.8108 | 18.3913 | 2.1485 | 0.84322 | 843.22 | 0.1386 |  | 8 | 18.9333 | 16.1648 | 2.0879 | 0.85378 | 853.78 | 0.13771 |  | 0 | 18.9901 | 16.3137 | 2.0577 | 0.85906 | 859.06 | 0.13817 | 0 | 18.9901 | 16.3137 | 2.0577 | 0.85906 | 859.06 | 0.13817 | 6 | 9.696 | 8.2911 | 2.0804 | 0.8551 | 855.1 | 0.13995 | 12 | 321.3772 | 273.537 | 2.1031 | 0.85114 | 851.14 | 0.15953
[8 empty] | 25 | 20.9213 | 17.6274 | 2.1523 | 0.84256 | 842.56 | 0.13853 |  | 9 | 18.1501 | 15.4842 | 2.0917 | 0.85312 | 853.12 | 0.13766 |  | 1 | 18.1727 | 15.5994 | 2.0615 | 0.8584 | 858.4 | 0.13811 | 1 | 18.1727 | 15.5994 | 2.0615 | 0.8584 | 858.4 | 0.13811 | 7 | 9.3603 | 7.9978 | 2.0842 | 0.85444 | 854.44 | 0.13987 | 13 | 300.2156 | 255.3273 | 2.1069 | 0.85048 | 850.48 | 0.15949
[8 empty] | 26 | 20.0805 | 16.9058 | 2.156 | 0.8419 | 841.9 | 0.13845 |  | 10 | 17.4107 | 14.8419 | 2.0955 | 0.85246 | 852.46 | 0.1376 |  | 2 | 17.4028 | 14.9271 | 2.0652 | 0.85774 | 857.74 | 0.13805 | 2 | 17.4028 | 14.9271 | 2.0652 | 0.85774 | 857.74 | 0.13805 | 8 | 9.0409 | 7.719 | 2.0879 | 0.85378 | 853.78 | 0.1398 | 14 | 280.7348 | 238.5741 | 2.1106 | 0.84982 | 849.82 | 0.15945
[8 empty] | 27 | 19.2853 | 16.2236 | 2.1598 | 0.84124 | 841.24 | 0.13837 |  | 11 | 16.7123 | 14.2355 | 2.0993 | 0.8518 | 851.8 | 0.13754 |  | 3 | 16.6772 | 14.2937 | 2.069 | 0.85708 | 857.08 | 0.138 | 3 | 16.6772 | 14.2937 | 2.069 | 0.85708 | 857.08 | 0.138 | 9 | 8.7371 | 7.4538 | 2.0917 | 0.85312 | 853.12 | 0.13972 | 15 | 262.7821 | 223.1441 | 2.1144 | 0.84916 | 849.16 | 0.15942
[8 empty] | 28 | 18.5326 | 15.5781 | 2.1636 | 0.84058 | 840.58 | 0.1383 |  | 12 | 16.052 | 13.6625 | 2.1031 | 0.85114 | 851.14 | 0.13749 |  | 4 | 15.9927 | 13.6964 | 2.0728 | 0.85642 | 856.42 | 0.13794 | 4 | 15.9927 | 13.6964 | 2.0728 | 0.85642 | 856.42 | 0.13794 | 10 | 8.4477 | 7.2013 | 2.0955 | 0.85246 | 852.46 | 0.13965 | 16 | 246.2201 | 208.9178 | 2.1182 | 0.8485 | 848.5 | 0.15938
[8 empty] | 29 | 17.8196 | 14.9671 | 2.1674 | 0.83992 | 839.92 | 0.13822 |  | 13 | 15.4273 | 13.1206 | 2.1069 | 0.85048 | 850.48 | 0.13743 |  | 5 | 15.3465 | 13.1329 | 2.0766 | 0.85576 | 855.76 | 0.13788 | 5 | 15.3465 | 13.1329 | 2.0766 | 0.85576 | 855.76 | 0.13788 | 11 | 8.172 | 6.9609 | 2.0993 | 0.8518 | 851.8 | 0.13958 | 17 | 230.9252 | 195.7877 | 2.122 | 0.84784 | 847.84 | 0.15934
[8 empty] | 30 | 17.1439 | 14.3882 | 2.1712 | 0.83926 | 839.26 | 0.13815 |  | 14 | 14.8359 | 12.6078 | 2.1106 | 0.84982 | 849.82 | 0.13737 |  | 6 | 14.736 | 12.6007 | 2.0804 | 0.8551 | 855.1 | 0.13783 | 6 | 14.736 | 12.6007 | 2.0804 | 0.8551 | 855.1 | 0.13783 | 12 | 7.9092 | 6.7318 | 2.1031 | 0.85114 | 851.14 | 0.1395 | 18 | 216.7861 | 183.6568 | 2.1258 | 0.84718 | 847.18 | 0.1593
[8 empty] | 31 | 16.5031 | 13.8395 | 2.175 | 0.8386 | 838.6 | 0.13808 |  | 15 | 14.2756 | 12.1222 | 2.1144 | 0.84916 | 849.16 | 0.13732 |  | 7 | 14.1588 | 12.0978 | 2.0842 | 0.85444 | 854.44 | 0.13777 | 7 | 14.1588 | 12.0978 | 2.0842 | 0.85444 | 854.44 | 0.13777 | 13 | 7.6584 | 6.5134 | 2.1069 | 0.85048 | 850.48 | 0.13942 | 19 | 203.7023 | 172.438 | 2.1296 | 0.84652 | 846.52 | 0.15926
[8 empty] | 32 | 15.8949 | 13.3189 | 2.1787 | 0.83794 | 837.94 | 0.138 |  | 16 | 13.7444 | 11.6621 | 2.1182 | 0.8485 | 848.5 | 0.13726 |  | 8 | 13.6127 | 11.6222 | 2.0879 | 0.85378 | 853.78 | 0.13771 | 8 | 13.6127 | 11.6222 | 2.0879 | 0.85378 | 853.78 | 0.13771 | 14 | 7.4191 | 6.3049 | 2.1106 | 0.84982 | 849.82 | 0.13935 | 20 | 191.583 | 162.0524 | 2.1333 | 0.84586 | 845.86 | 0.15922
[8 empty] | 33 | 15.3173 | 12.8249 | 2.1825 | 0.83728 | 837.28 | 0.13792 |  | 17 | 13.2404 | 11.2258 | 2.122 | 0.84784 | 847.84 | 0.1372 |  | 9 | 13.0956 | 11.1721 | 2.0917 | 0.85312 | 853.12 | 0.13766 | 9 | 13.0956 | 11.1721 | 2.0917 | 0.85312 | 853.12 | 0.13766 | 15 | 7.1906 | 6.106 | 2.1144 | 0.84916 | 849.16 | 0.13927 | 21 | 180.3465 | 152.4289 | 2.1371 | 0.8452 | 845.2 | 0.15918
[8 empty] | 34 | 14.7685 | 12.3557 | 2.1863 | 0.83662 | 836.62 | 0.13785 |  | 18 | 12.762 | 10.8118 | 2.1258 | 0.84718 | 847.18 | 0.13715 |  | 10 | 12.6057 | 10.7458 | 2.0955 | 0.85246 | 852.46 | 0.1376 | 10 | 12.6057 | 10.7458 | 2.0955 | 0.85246 | 852.46 | 0.1376 | 16 | 6.9722 | 5.9159 | 2.1182 | 0.8485 | 848.5 | 0.1392 | 22 | 169.9184 | 143.5029 | 2.1409 | 0.84454 | 844.54 | 0.15914
[8 empty] | 35 | 14.2468 | 11.9097 | 2.1901 | 0.83596 | 835.96 | 0.13777 |  | 19 | 12.3076 | 10.4186 | 2.1296 | 0.84652 | 846.52 | 0.13709 |  | 11 | 12.1411 | 10.3418 | 2.0993 | 0.8518 | 851.8 | 0.13754 | 11 | 12.1411 | 10.3418 | 2.0993 | 0.8518 | 851.8 | 0.13754 | 17 | 6.7634 | 5.7343 | 2.122 | 0.84784 | 847.84 | 0.13912 | 23 | 160.2316 | 135.2162 | 2.1447 | 0.84388 | 843.88 | 0.1591
[8 empty] | 36 | 13.7504 | 11.4857 | 2.1939 | 0.8353 | 835.3 | 0.1377 |  | 20 | 11.8757 | 10.0452 | 2.1333 | 0.84586 | 845.86 | 0.13703 |  | 12 | 11.7004 | 9.9587 | 2.1031 | 0.85114 | 851.14 | 0.13749 | 12 | 11.7004 | 9.9587 | 2.1031 | 0.85114 | 851.14 | 0.13749 | 18 | 6.5637 | 5.5606 | 2.1258 | 0.84718 | 847.18 | 0.13905 | 24 | 151.2251 | 127.516 | 2.1485 | 0.84322 | 843.22 | 0.15906
[8 empty] | 37 | 13.2779 | 11.0822 | 2.1977 | 0.83464 | 834.64 | 0.13762 |  | 21 | 11.4649 | 9.6901 | 2.1371 | 0.8452 | 845.2 | 0.13698 |  | 13 | 11.2819 | 9.595 | 2.1069 | 0.85048 | 850.48 | 0.13743 | 13 | 11.2819 | 9.595 | 2.1069 | 0.85048 | 850.48 | 0.13743 | 19 | 6.3726 | 5.3945 | 2.1296 | 0.84652 | 846.52 | 0.13897 | 25 | 142.8436 | 120.3543 | 2.1523 | 0.84256 | 842.56 | 0.15902
[8 empty] | 38 | 12.8278 | 10.6982 | 2.2014 | 0.83398 | 833.98 | 0.13755 |  | 22 | 11.0739 | 9.3523 | 2.1409 | 0.84454 | 844.54 | 0.13692 |  | 14 | 10.8843 | 9.2497 | 2.1106 | 0.84982 | 849.82 | 0.13737 | 14 | 10.8843 | 9.2497 | 2.1106 | 0.84982 | 849.82 | 0.13737 | 20 | 6.1895 | 5.2355 | 2.1333 | 0.84586 | 845.86 | 0.1389 | 26 | 135.0369 | 113.6875 | 2.156 | 0.8419 | 841.9 | 0.15899
[8 empty] | 39 | 12.3989 | 10.3323 | 2.2052 | 0.83332 | 833.32 | 0.13747 |  | 23 | 10.7016 | 9.0309 | 2.1447 | 0.84388 | 843.88 | 0.13686 |  | 15 | 10.5064 | 8.9216 | 2.1144 | 0.84916 | 849.16 | 0.13732 | 15 | 10.5064 | 8.9216 | 2.1144 | 0.84916 | 849.16 | 0.13732 | 21 | 6.0142 | 5.0832 | 2.1371 | 0.8452 | 845.2 | 0.13883 | 27 | 127.7591 | 107.4761 | 2.1598 | 0.84124 | 841.24 | 0.15895
[8 empty] | 40 | 11.99 | 9.9836 | 2.209 | 0.83266 | 832.66 | 0.1374 |  | 24 | 10.3469 | 8.7247 | 2.1485 | 0.84322 | 843.22 | 0.13681 |  | 16 | 10.1469 | 8.6096 | 2.1182 | 0.8485 | 848.5 | 0.13726 | 16 | 10.1469 | 8.6096 | 2.1182 | 0.8485 | 848.5 | 0.13726 | 22 | 5.8461 | 4.9373 | 2.1409 | 0.84454 | 844.54 | 0.13875 | 28 | 120.9687 | 101.6838 | 2.1636 | 0.84058 | 840.58 | 0.15891
[8 empty] | 41 | 11.5998 | 9.6511 | 2.2128 | 0.832 | 832 | 0.13733 |  | 25 | 10.0087 | 8.4329 | 2.1523 | 0.84256 | 842.56 | 0.13675 |  | 17 | 9.8046 | 8.3128 | 2.122 | 0.84784 | 847.84 | 0.1372 | 17 | 9.8046 | 8.3128 | 2.122 | 0.84784 | 847.84 | 0.1372 | 23 | 5.685 | 4.7974 | 2.1447 | 0.84388 | 843.88 | 0.13867 | 29 | 114.6276 | 96.278 | 2.1674 | 0.83992 | 839.92 | 0.15887
[8 empty] | 42 | 11.2274 | 9.3338 | 2.2166 | 0.83134 | 831.34 | 0.13725 |  | 26 | 9.6861 | 8.1547 | 2.156 | 0.8419 | 841.9 | 0.13669 |  | 18 | 9.4787 | 8.0302 | 2.1258 | 0.84718 | 847.18 | 0.13715 | 18 | 9.4787 | 8.0302 | 2.1258 | 0.84718 | 847.18 | 0.13715 | 24 | 5.5303 | 4.6633 | 2.1485 | 0.84322 | 843.22 | 0.1386 | 30 | 108.7013 | 91.2287 | 2.1712 | 0.83926 | 839.26 | 0.15883
[8 empty] | 43 | 10.8718 | 9.0309 | 2.2204 | 0.83068 | 830.68 | 0.13717 |  | 27 | 9.3782 | 7.8893 | 2.1598 | 0.84124 | 841.24 | 0.13664 |  | 19 | 9.1681 | 7.761 | 2.1296 | 0.84652 | 846.52 | 0.13709 | 19 | 9.1681 | 7.761 | 2.1296 | 0.84652 | 846.52 | 0.13709 | 25 | 5.3819 | 4.5346 | 2.1523 | 0.84256 | 842.56 | 0.13853 | 31 | 103.1581 | 86.5084 | 2.175 | 0.8386 | 838.6 | 0.15879
[8 empty] | 44 | 10.5319 | 8.7417 | 2.2241 | 0.83002 | 830.02 | 0.1371 |  | 28 | 9.0842 | 7.636 | 2.1636 | 0.84058 | 840.58 | 0.13658 |  | 20 | 8.8719 | 7.5044 | 2.1333 | 0.84586 | 845.86 | 0.13703 | 20 | 8.8719 | 7.5044 | 2.1333 | 0.84586 | 845.86 | 0.13703 | 26 | 5.2394 | 4.411 | 2.156 | 0.8419 | 841.9 | 0.13845 | 32 | 97.9692 | 82.0923 | 2.1787 | 0.83794 | 837.94 | 0.15875
[8 empty] | 45 | 10.207 | 8.4652 | 2.2279 | 0.82936 | 829.36 | 0.13703 |  | 29 | 8.8033 | 7.394 | 2.1674 | 0.83992 | 839.92 | 0.13652 |  | 21 | 8.5894 | 7.2597 | 2.1371 | 0.8452 | 845.2 | 0.13698 | 21 | 8.5894 | 7.2597 | 2.1371 | 0.8452 | 845.2 | 0.13698 | 27 | 5.1025 | 4.2924 | 2.1598 | 0.84124 | 841.24 | 0.13837 | 33 | 93.108 | 77.9575 | 2.1825 | 0.83728 | 837.28 | 0.15871
[8 empty] | 46 | 9.8962 | 8.201 | 2.2317 | 0.8287 | 828.7 | 0.13695 |  | 30 | 8.5347 | 7.1628 | 2.1712 | 0.83926 | 839.26 | 0.13647 |  | 22 | 8.3196 | 7.0262 | 2.1409 | 0.84454 | 844.54 | 0.13692 | 22 | 8.3196 | 7.0262 | 2.1409 | 0.84454 | 844.54 | 0.13692 | 28 | 4.9709 | 4.1784 | 2.1636 | 0.84058 | 840.58 | 0.1383 | 34 | 88.5504 | 74.083 | 2.1863 | 0.83662 | 836.62 | 0.15867
[8 empty] | 47 | 9.5988 | 7.9482 | 2.2355 | 0.82804 | 828.04 | 0.13687 |  | 31 | 8.2779 | 6.9418 | 2.175 | 0.8386 | 838.6 | 0.13641 |  | 23 | 8.062 | 6.8033 | 2.1447 | 0.84388 | 843.88 | 0.13686 | 23 | 8.062 | 6.8033 | 2.1447 | 0.84388 | 843.88 | 0.13686 | 29 | 4.8443 | 4.0688 | 2.1674 | 0.83992 | 839.92 | 0.13822 | 35 | 84.2741 | 70.4498 | 2.1901 | 0.83596 | 835.96 | 0.15863
[8 empty] | 48 | 9.314 | 7.7062 | 2.2393 | 0.82738 | 827.38 | 0.1368 |  | 32 | 8.0321 | 6.7304 | 2.1787 | 0.83794 | 837.94 | 0.13635 |  | 24 | 7.8157 | 6.5904 | 2.1485 | 0.84322 | 843.22 | 0.13681 | 24 | 7.8157 | 6.5904 | 2.1485 | 0.84322 | 843.22 | 0.13681 | 30 | 4.7226 | 3.9635 | 2.1712 | 0.83926 | 839.26 | 0.13815 | 36 | 80.2588 | 67.0402 | 2.1939 | 0.8353 | 835.3 | 0.1586
[8 empty] | 49 | 9.0412 | 7.4746 | 2.2431 | 0.82672 | 826.72 | 0.13672 |  | 33 | 7.7967 | 6.5281 | 2.1825 | 0.83728 | 837.28 | 0.1363 |  | 25 | 7.5803 | 6.3869 | 2.1523 | 0.84256 | 842.56 | 0.13675 | 25 | 7.5803 | 6.3869 | 2.1523 | 0.84256 | 842.56 | 0.13675 | 31 | 4.6054 | 3.8621 | 2.175 | 0.8386 | 838.6 | 0.13808 | 37 | 76.4858 | 63.8381 | 2.1977 | 0.83464 | 834.64 | 0.15856
[8 empty] | 50 | 8.7798 | 7.2527 | 2.2468 | 0.82606 | 826.06 | 0.13665 |  | 34 | 7.5713 | 6.3343 | 2.1863 | 0.83662 | 836.62 | 0.13624 |  | 26 | 7.3551 | 6.1923 | 2.156 | 0.8419 | 841.9 | 0.13669 | 26 | 7.3551 | 6.1923 | 2.156 | 0.8419 | 841.9 | 0.13669 | 32 | 4.4926 | 3.7645 | 2.1787 | 0.83794 | 837.94 | 0.138 | 38 | 72.9379 | 60.8288 | 2.2014 | 0.83398 | 833.98 | 0.15852
[8 empty] | 51 | 8.5292 | 7.04 | 2.2506 | 0.8254 | 825.4 | 0.13658 |  | 35 | 7.3553 | 6.1488 | 2.1901 | 0.83596 | 835.96 | 0.13618 |  | 27 | 7.1395 | 6.0061 | 2.1598 | 0.84124 | 841.24 | 0.13664 | 27 | 7.1395 | 6.0061 | 2.1598 | 0.84124 | 841.24 | 0.13664 | 33 | 4.384 | 3.6706 | 2.1825 | 0.83728 | 837.28 | 0.13792 | 39 | 69.5994 | 57.9986 | 2.2052 | 0.83332 | 833.32 | 0.15848
[8 empty] | 52 | 8.2888 | 6.8361 | 2.2544 | 0.82474 | 824.74 | 0.1365 |  | 36 | 7.1482 | 5.9709 | 2.1939 | 0.8353 | 835.3 | 0.13613 |  | 28 | 6.9331 | 5.8278 | 2.1636 | 0.84058 | 840.58 | 0.13658 | 28 | 6.9331 | 5.8278 | 2.1636 | 0.84058 | 840.58 | 0.13658 | 34 | 4.2793 | 3.5801 | 2.1863 | 0.83662 | 836.62 | 0.13785 | 40 | 66.4556 | 55.3349 | 2.209 | 0.83266 | 832.66 | 0.15844
[8 empty] | 53 | 8.0581 | 6.6405 | 2.2582 | 0.82408 | 824.08 | 0.13642 |  | 37 | 6.9495 | 5.8004 | 2.1977 | 0.83464 | 834.64 | 0.13607 |  | 29 | 6.7353 | 5.6571 | 2.1674 | 0.83992 | 839.92 | 0.13652 | 29 | 6.7353 | 5.6571 | 2.1674 | 0.83992 | 839.92 | 0.13652 | 35 | 4.1784 | 3.493 | 2.1901 | 0.83596 | 835.96 | 0.13777 | 41 | 63.4932 | 52.8264 | 2.2128 | 0.832 | 832 | 0.1584
[8 empty] | 54 | 7.8366 | 6.4528 | 2.262 | 0.82342 | 823.42 | 0.13635 |  | 38 | 6.7589 | 5.6368 | 2.2014 | 0.83398 | 833.98 | 0.13601 |  | 30 | 6.5457 | 5.4936 | 2.1712 | 0.83926 | 839.26 | 0.13647 | 30 | 6.5457 | 5.4936 | 2.1712 | 0.83926 | 839.26 | 0.13647 | 36 | 4.0811 | 3.4089 | 2.1939 | 0.8353 | 835.3 | 0.1377 | 42 | 60.6999 | 50.4622 | 2.2166 | 0.83134 | 831.34 | 0.15836
[8 empty] | 55 | 7.6239 | 6.2726 | 2.2658 | 0.82276 | 822.76 | 0.13627 |  | 39 | 6.5758 | 5.4798 | 2.2052 | 0.83332 | 833.32 | 0.13596 |  | 31 | 6.3639 | 5.3368 | 2.175 | 0.8386 | 838.6 | 0.13641 | 31 | 6.3639 | 5.3368 | 2.175 | 0.8386 | 838.6 | 0.13641 | 37 | 3.9872 | 3.3279 | 2.1977 | 0.83464 | 834.64 | 0.13762 | 43 | 58.0642 | 48.2327 | 2.2204 | 0.83068 | 830.68 | 0.15832
[8 empty] | 56 | 7.4195 | 6.0995 | 2.2695 | 0.8221 | 822.1 | 0.1362 |  | 40 | 6.4 | 5.329 | 2.209 | 0.83266 | 832.66 | 0.1359 |  | 32 | 6.1895 | 5.1864 | 2.1787 | 0.83794 | 837.94 | 0.13635 | 32 | 6.1895 | 5.1864 | 2.1787 | 0.83794 | 837.94 | 0.13635 | 38 | 3.8966 | 3.2497 | 2.2014 | 0.83398 | 833.98 | 0.13755 | 44 | 55.5756 | 46.1288 | 2.2241 | 0.83002 | 830.02 | 0.15828
[8 empty] | 57 | 7.223 | 5.9332 | 2.2733 | 0.82144 | 821.44 | 0.13612 |  | 41 | 6.231 | 5.1842 | 2.2128 | 0.832 | 832 | 0.13584 |  | 33 | 6.022 | 5.0421 | 2.1825 | 0.83728 | 837.28 | 0.1363 | 33 | 6.022 | 5.0421 | 2.1825 | 0.83728 | 837.28 | 0.1363 | 39 | 3.8092 | 3.1743 | 2.2052 | 0.83332 | 833.32 | 0.13747 | 45 | 53.2244 | 44.1422 | 2.2279 | 0.82936 | 829.36 | 0.15824
[8 empty] | 58 | 7.034 | 5.7734 | 2.2771 | 0.82078 | 820.78 | 0.13605 |  | 42 | 6.0686 | 5.0451 | 2.2166 | 0.83134 | 831.34 | 0.13579 |  | 34 | 5.8612 | 4.9036 | 2.1863 | 0.83662 | 836.62 | 0.13624 | 34 | 5.8612 | 4.9036 | 2.1863 | 0.83662 | 836.62 | 0.13624 | 40 | 3.7248 | 3.1015 | 2.209 | 0.83266 | 832.66 | 0.1374 | 46 | 51.0016 | 42.265 | 2.2317 | 0.8287 | 828.7 | 0.15821
[8 empty] | 59 | 6.8522 | 5.6197 | 2.2809 | 0.82012 | 820.12 | 0.13597 |  | 43 | 5.9124 | 4.9113 | 2.2204 | 0.83068 | 830.68 | 0.13573 |  | 35 | 5.7067 | 4.7706 | 2.1901 | 0.83596 | 835.96 | 0.13618 | 35 | 5.7067 | 4.7706 | 2.1901 | 0.83596 | 835.96 | 0.13618 | 41 | 3.6432 | 3.0311 | 2.2128 | 0.832 | 832 | 0.13733 | 47 | 48.8989 | 40.4902 | 2.2355 | 0.82804 | 828.04 | 0.15817
[8 empty] | 60 | 6.6773 | 5.4718 | 2.2847 | 0.81946 | 819.46 | 0.1359 |  | 44 | 5.7621 | 4.7827 | 2.2241 | 0.83002 | 830.02 | 0.13567 |  | 36 | 5.5583 | 4.6428 | 2.1939 | 0.8353 | 835.3 | 0.13613 | 36 | 5.5583 | 4.6428 | 2.1939 | 0.8353 | 835.3 | 0.13613 | 42 | 3.5644 | 2.9632 | 2.2166 | 0.83134 | 831.34 | 0.13725 | 48 | 46.9085 | 38.8112 | 2.2393 | 0.82738 | 827.38 | 0.15813
[8 empty] | 61 | 6.5088 | 5.3294 | 2.2885 | 0.8188 | 818.8 | 0.13583 |  | 45 | 5.6175 | 4.6589 | 2.2279 | 0.82936 | 829.36 | 0.13562 |  | 37 | 5.4155 | 4.52 | 2.1977 | 0.83464 | 834.64 | 0.13607 | 37 | 5.4155 | 4.52 | 2.1977 | 0.83464 | 834.64 | 0.13607 | 43 | 3.4882 | 2.8976 | 2.2204 | 0.83068 | 830.68 | 0.13717 | 49 | 45.0234 | 37.2218 | 2.2431 | 0.82672 | 826.72 | 0.15809
[8 empty] | 62 | 6.3466 | 5.1924 | 2.2922 | 0.81814 | 818.14 | 0.13575 |  | 46 | 5.4782 | 4.5398 | 2.2317 | 0.8287 | 828.7 | 0.13556 |  | 38 | 5.2781 | 4.4019 | 2.2014 | 0.83398 | 833.98 | 0.13601 | 38 | 5.2781 | 4.4019 | 2.2014 | 0.83398 | 833.98 | 0.13601 | 44 | 3.4145 | 2.8341 | 2.2241 | 0.83002 | 830.02 | 0.1371 | 50 | 43.237 | 35.7163 | 2.2468 | 0.82606 | 826.06 | 0.15805
[8 empty] | 63 | 6.1903 | 5.0604 | 2.296 | 0.81748 | 817.48 | 0.13567 |  | 47 | 5.344 | 4.425 | 2.2355 | 0.82804 | 828.04 | 0.1355 |  | 39 | 5.1459 | 4.2882 | 2.2052 | 0.83332 | 833.32 | 0.13596 | 39 | 5.1459 | 4.2882 | 2.2052 | 0.83332 | 833.32 | 0.13596 | 45 | 3.3432 | 2.7727 | 2.2279 | 0.82936 | 829.36 | 0.13703 | 51 | 41.543 | 34.2896 | 2.2506 | 0.8254 | 825.4 | 0.15801
[8 empty] | 64 | 6.0396 | 4.9333 | 2.2998 | 0.81682 | 816.82 | 0.1356 |  | 48 | 5.2147 | 4.3145 | 2.2393 | 0.82738 | 827.38 | 0.13545 |  | 40 | 5.0187 | 4.1789 | 2.209 | 0.83266 | 832.66 | 0.1359 | 40 | 5.0187 | 4.1789 | 2.209 | 0.83266 | 832.66 | 0.1359 | 46 | 3.2742 | 2.7134 | 2.2317 | 0.8287 | 828.7 | 0.13695 | 52 | 39.9357 | 32.9366 | 2.2544 | 0.82474 | 824.74 | 0.15797
[8 empty] | 65 | 5.8943 | 4.8107 | 2.3036 | 0.81616 | 816.16 | 0.13553 |  | 49 | 5.09 | 4.208 | 2.2431 | 0.82672 | 826.72 | 0.13539 |  | 41 | 4.8961 | 4.0736 | 2.2128 | 0.832 | 832 | 0.13584 | 41 | 4.8961 | 4.0736 | 2.2128 | 0.832 | 832 | 0.13584 | 47 | 3.2075 | 2.6559 | 2.2355 | 0.82804 | 828.04 | 0.13687 | 53 | 38.4099 | 31.6528 | 2.2582 | 0.82408 | 824.08 | 0.15793
[8 empty] | 66 | 5.7542 | 4.6925 | 2.3074 | 0.8155 | 815.5 | 0.13545 |  | 50 | 4.9698 | 4.1054 | 2.2468 | 0.82606 | 826.06 | 0.13533 |  | 42 | 4.778 | 3.9722 | 2.2166 | 0.83134 | 831.34 | 0.13579 | 42 | 4.778 | 3.9722 | 2.2166 | 0.83134 | 831.34 | 0.13579 | 48 | 3.1428 | 2.6003 | 2.2393 | 0.82738 | 827.38 | 0.1368 | 54 | 36.9606 | 30.4341 | 2.262 | 0.82342 | 823.42 | 0.15789
[8 empty] | 67 | 5.619 | 4.5786 | 2.3112 | 0.81484 | 814.84 | 0.13537 |  | 51 | 4.8539 | 4.0064 | 2.2506 | 0.8254 | 825.4 | 0.13528 |  | 43 | 4.6642 | 3.8744 | 2.2204 | 0.83068 | 830.68 | 0.13573 | 43 | 4.6642 | 3.8744 | 2.2204 | 0.83068 | 830.68 | 0.13573 | 49 | 3.0802 | 2.5465 | 2.2431 | 0.82672 | 826.72 | 0.13672 | 55 | 35.5833 | 29.2765 | 2.2658 | 0.82276 | 822.76 | 0.15785
[8 empty] | 68 | 5.4884 | 4.4686 | 2.3149 | 0.81418 | 814.18 | 0.1353 |  | 52 | 4.7419 | 3.9109 | 2.2544 | 0.82474 | 824.74 | 0.13522 |  | 44 | 4.5544 | 3.7803 | 2.2241 | 0.83002 | 830.02 | 0.13567 | 44 | 4.5544 | 3.7803 | 2.2241 | 0.83002 | 830.02 | 0.13567 | 50 | 3.0196 | 2.4943 | 2.2468 | 0.82606 | 826.06 | 0.13665 | 56 | 34.2736 | 28.1763 | 2.2695 | 0.8221 | 822.1 | 0.15782
[8 empty] | 69 | 5.3624 | 4.3624 | 2.3187 | 0.81352 | 813.52 | 0.13522 |  | 53 | 4.6339 | 3.8187 | 2.2582 | 0.82408 | 824.08 | 0.13516 |  | 45 | 4.4485 | 3.6894 | 2.2279 | 0.82936 | 829.36 | 0.13562 | 45 | 4.4485 | 3.6894 | 2.2279 | 0.82936 | 829.36 | 0.13562 | 51 | 2.9608 | 2.4438 | 2.2506 | 0.8254 | 825.4 | 0.13658 | 57 | 33.0276 | 27.1302 | 2.2733 | 0.82144 | 821.44 | 0.15778
[8 empty] | 70 | 5.2407 | 4.2599 | 2.3225 | 0.81286 | 812.86 | 0.13515 |  | 54 | 4.5296 | 3.7297 | 2.262 | 0.82342 | 823.42 | 0.13511 |  | 46 | 4.3464 | 3.6018 | 2.2317 | 0.8287 | 828.7 | 0.13556 | 46 | 4.3464 | 3.6018 | 2.2317 | 0.8287 | 828.7 | 0.13556 | 52 | 2.9038 | 2.3949 | 2.2544 | 0.82474 | 824.74 | 0.1365 | 58 | 31.8415 | 26.1349 | 2.2771 | 0.82078 | 820.78 | 0.15774
[8 empty] | 71 | 5.1231 | 4.1609 | 2.3263 | 0.8122 | 812.2 | 0.13508 |  | 55 | 4.4287 | 3.6438 | 2.2658 | 0.82276 | 822.76 | 0.13505 |  | 47 | 4.2477 | 3.5173 | 2.2355 | 0.82804 | 828.04 | 0.1355 | 47 | 4.2477 | 3.5173 | 2.2355 | 0.82804 | 828.04 | 0.1355 | 53 | 2.8485 | 2.3474 | 2.2582 | 0.82408 | 824.08 | 0.13642 | 59 | 30.7119 | 25.1875 | 2.2809 | 0.82012 | 820.12 | 0.1577
[8 empty] | 72 | 5.0094 | 4.0653 | 2.3301 | 0.81154 | 811.54 | 0.135 |  | 56 | 4.3313 | 3.5608 | 2.2695 | 0.8221 | 822.1 | 0.13499 |  | 48 | 4.1525 | 3.4357 | 2.2393 | 0.82738 | 827.38 | 0.13545 | 48 | 4.1525 | 3.4357 | 2.2393 | 0.82738 | 827.38 | 0.13545 | 54 | 2.795 | 2.3014 | 2.262 | 0.82342 | 823.42 | 0.13635 | 60 | 29.6356 | 24.2852 | 2.2847 | 0.81946 | 819.46 | 0.15766
[8 empty] | 73 | 4.8994 | 3.9729 | 2.3338 | 0.81088 | 810.88 | 0.13492 |  | 57 | 4.2372 | 3.4806 | 2.2733 | 0.82144 | 821.44 | 0.13494 |  | 49 | 4.0605 | 3.3569 | 2.2431 | 0.82672 | 826.72 | 0.13539 | 49 | 4.0605 | 3.3569 | 2.2431 | 0.82672 | 826.72 | 0.13539 | 55 | 2.743 | 2.2568 | 2.2658 | 0.82276 | 822.76 | 0.13627 | 61 | 28.6095 | 23.4254 | 2.2885 | 0.8188 | 818.8 | 0.15762
[8 empty] | 74 | 4.7931 | 3.8835 | 2.3376 | 0.81022 | 810.22 | 0.13485 |  | 58 | 4.1461 | 3.403 | 2.2771 | 0.82078 | 820.78 | 0.13488 |  | 50 | 3.9716 | 3.2808 | 2.2468 | 0.82606 | 826.06 | 0.13533 | 50 | 3.9716 | 3.2808 | 2.2468 | 0.82606 | 826.06 | 0.13533 | 56 | 2.6925 | 2.2135 | 2.2695 | 0.8221 | 822.1 | 0.1362 | 62 | 27.6308 | 22.6058 | 2.2922 | 0.81814 | 818.14 | 0.15758
[8 empty] | 75 | 4.6903 | 3.7971 | 2.3414 | 0.80956 | 809.56 | 0.13477 |  | 59 | 4.058 | 3.3281 | 2.2809 | 0.82012 | 820.12 | 0.13482 |  | 51 | 3.8857 | 3.2072 | 2.2506 | 0.8254 | 825.4 | 0.13528 | 51 | 3.8857 | 3.2072 | 2.2506 | 0.8254 | 825.4 | 0.13528 | 57 | 2.6435 | 2.1715 | 2.2733 | 0.82144 | 821.44 | 0.13612 | 63 | 26.6968 | 21.8241 | 2.296 | 0.81748 | 817.48 | 0.15754
[8 empty] | 76 | 4.5908 | 3.7135 | 2.3452 | 0.8089 | 808.9 | 0.1347 |  | 60 | 3.9728 | 3.2555 | 2.2847 | 0.81946 | 819.46 | 0.13477 |  | 52 | 3.8026 | 3.1361 | 2.2544 | 0.82474 | 824.74 | 0.13522 | 52 | 3.8026 | 3.1361 | 2.2544 | 0.82474 | 824.74 | 0.13522 | 58 | 2.5959 | 2.1307 | 2.2771 | 0.82078 | 820.78 | 0.13605 | 64 | 25.8052 | 21.0782 | 2.2998 | 0.81682 | 816.82 | 0.1575
[8 empty] | 77 | 4.4944 | 3.6326 | 2.349 | 0.80824 | 808.24 | 0.13462 |  | 61 | 3.8903 | 3.1853 | 2.2885 | 0.8188 | 818.8 | 0.13471 |  | 53 | 3.7222 | 3.0674 | 2.2582 | 0.82408 | 824.08 | 0.13516 | 53 | 3.7222 | 3.0674 | 2.2582 | 0.82408 | 824.08 | 0.13516 | 59 | 2.5497 | 2.0911 | 2.2809 | 0.82012 | 820.12 | 0.13597 | 65 | 24.9535 | 20.3661 | 2.3036 | 0.81616 | 816.16 | 0.15746
[8 empty] | 78 | 4.4011 | 3.5543 | 2.3528 | 0.80758 | 807.58 | 0.13455 |  | 62 | 3.8104 | 3.1174 | 2.2922 | 0.81814 | 818.14 | 0.13465 |  | 54 | 3.6445 | 3.0009 | 2.262 | 0.82342 | 823.42 | 0.13511 | 54 | 3.6445 | 3.0009 | 2.262 | 0.82342 | 823.42 | 0.13511 | 60 | 2.5048 | 2.0526 | 2.2847 | 0.81946 | 819.46 | 0.1359 | 66 | 24.1397 | 19.6859 | 2.3074 | 0.8155 | 815.5 | 0.15743
[8 empty] | 79 | 4.3107 | 3.4784 | 2.3566 | 0.80692 | 806.92 | 0.13447 |  | 63 | 3.733 | 3.0517 | 2.296 | 0.81748 | 817.48 | 0.1346 |  | 55 | 3.5692 | 2.9366 | 2.2658 | 0.82276 | 822.76 | 0.13505 | 55 | 3.5692 | 2.9366 | 2.2658 | 0.82276 | 822.76 | 0.13505 | 61 | 2.4612 | 2.0153 | 2.2885 | 0.8188 | 818.8 | 0.13583 | 67 | 23.3616 | 19.036 | 2.3112 | 0.81484 | 814.84 | 0.15739
[8 empty] | 80 | 4.2232 | 3.405 | 2.3603 | 0.80626 | 806.26 | 0.1344 |  | 64 | 3.658 | 2.988 | 2.2998 | 0.81682 | 816.82 | 0.13454 |  | 56 | 3.4963 | 2.8743 | 2.2695 | 0.8221 | 822.1 | 0.13499 | 56 | 3.4963 | 2.8743 | 2.2695 | 0.8221 | 822.1 | 0.13499 | 62 | 2.4188 | 1.9789 | 2.2922 | 0.81814 | 818.14 | 0.13575 | 68 | 22.6174 | 18.4146 | 2.3149 | 0.81418 | 814.18 | 0.15735
[8 empty] | 81 | 4.1383 | 3.3338 | 2.3641 | 0.8056 | 805.6 | 0.13432 |  | 65 | 3.5854 | 2.9263 | 2.3036 | 0.81616 | 816.16 | 0.13448 |  | 57 | 3.4257 | 2.814 | 2.2733 | 0.82144 | 821.44 | 0.13494 | 57 | 3.4257 | 2.814 | 2.2733 | 0.82144 | 821.44 | 0.13494 | 63 | 2.3776 | 1.9437 | 2.296 | 0.81748 | 817.48 | 0.13567 | 69 | 21.9052 | 17.8203 | 2.3187 | 0.81352 | 813.52 | 0.15731
[8 empty] | 82 | 4.0561 | 3.2649 | 2.3679 | 0.80494 | 804.94 | 0.13425 |  | 66 | 3.515 | 2.8665 | 2.3074 | 0.8155 | 815.5 | 0.13443 |  | 58 | 3.3574 | 2.7557 | 2.2771 | 0.82078 | 820.78 | 0.13488 | 58 | 3.3574 | 2.7557 | 2.2771 | 0.82078 | 820.78 | 0.13488 | 64 | 2.3375 | 1.9093 | 2.2998 | 0.81682 | 816.82 | 0.1356 | 70 | 21.2235 | 17.2517 | 2.3225 | 0.81286 | 812.86 | 0.15727
[8 empty] | 83 | 3.9763 | 3.1981 | 2.3717 | 0.80428 | 804.28 | 0.13417 |  | 67 | 3.4467 | 2.8085 | 2.3112 | 0.81484 | 814.84 | 0.13437 |  | 59 | 3.2911 | 2.6991 | 2.2809 | 0.82012 | 820.12 | 0.13482 | 59 | 3.2911 | 2.6991 | 2.2809 | 0.82012 | 820.12 | 0.13482 | 65 | 2.2985 | 1.876 | 2.3036 | 0.81616 | 816.16 | 0.13553 | 71 | 20.5706 | 16.7074 | 2.3263 | 0.8122 | 812.2 | 0.15723
[8 empty] | 84 | 3.8989 | 3.1333 | 2.3755 | 0.80362 | 803.62 | 0.1341 |  | 68 | 3.3805 | 2.7523 | 2.3149 | 0.81418 | 814.18 | 0.13431 |  | 60 | 3.2269 | 2.6443 | 2.2847 | 0.81946 | 819.46 | 0.13477 | 60 | 3.2269 | 2.6443 | 2.2847 | 0.81946 | 819.46 | 0.13477 | 66 | 2.2606 | 1.8435 | 2.3074 | 0.8155 | 815.5 | 0.13545 | 72 | 19.945 | 16.1862 | 2.3301 | 0.81154 | 811.54 | 0.15719
[8 empty] | 85 | 3.8239 | 3.0704 | 2.3793 | 0.80296 | 802.96 | 0.13403 |  | 69 | 3.3162 | 2.6978 | 2.3187 | 0.81352 | 813.52 | 0.13426 |  | 61 | 3.1646 | 2.5912 | 2.2885 | 0.8188 | 818.8 | 0.13471 | 61 | 3.1646 | 2.5912 | 2.2885 | 0.8188 | 818.8 | 0.13471 | 67 | 2.2237 | 1.812 | 2.3112 | 0.81484 | 814.84 | 0.13537 | 73 | 19.3454 | 15.6868 | 2.3338 | 0.81088 | 810.88 | 0.15715
[8 empty] | 86 | 3.751 | 3.0094 | 2.383 | 0.8023 | 802.3 | 0.13395 |  | 70 | 3.2539 | 2.645 | 2.3225 | 0.81286 | 812.86 | 0.1342 |  | 62 | 3.1043 | 2.5397 | 2.2922 | 0.81814 | 818.14 | 0.13465 | 62 | 3.1043 | 2.5397 | 2.2922 | 0.81814 | 818.14 | 0.13465 | 68 | 2.1878 | 1.7812 | 2.3149 | 0.81418 | 814.18 | 0.1353 | 74 | 18.7704 | 15.2082 | 2.3376 | 0.81022 | 810.22 | 0.15711
[8 empty] | 87 | 3.6803 | 2.9503 | 2.3868 | 0.80164 | 801.64 | 0.13387 |  | 71 | 3.1934 | 2.5937 | 2.3263 | 0.8122 | 812.2 | 0.13414 |  | 63 | 3.0457 | 2.4898 | 2.296 | 0.81748 | 817.48 | 0.1346 | 63 | 3.0457 | 2.4898 | 2.296 | 0.81748 | 817.48 | 0.1346 | 69 | 2.1528 | 1.7513 | 2.3187 | 0.81352 | 813.52 | 0.13522 | 75 | 18.2188 | 14.7492 | 2.3414 | 0.80956 | 809.56 | 0.15707
[8 empty] | 88 | 3.6116 | 2.8928 | 2.3906 | 0.80098 | 800.98 | 0.1338 |  | 72 | 3.1346 | 2.5439 | 2.3301 | 0.81154 | 811.54 | 0.13409 |  | 64 | 2.9888 | 2.4413 | 2.2998 | 0.81682 | 816.82 | 0.13454 | 64 | 2.9888 | 2.4413 | 2.2998 | 0.81682 | 816.82 | 0.13454 | 70 | 2.1187 | 1.7222 | 2.3225 | 0.81286 | 812.86 | 0.13515 | 76 | 17.6894 | 14.309 | 2.3452 | 0.8089 | 808.9 | 0.15704
[8 empty] | 89 | 3.5449 | 2.8371 | 2.3944 | 0.80032 | 800.32 | 0.13372 |  | 73 | 3.0775 | 2.4955 | 2.3338 | 0.81088 | 810.88 | 0.13403 |  | 65 | 2.9336 | 2.3943 | 2.3036 | 0.81616 | 816.16 | 0.13448 | 65 | 2.9336 | 2.3943 | 2.3036 | 0.81616 | 816.16 | 0.13448 | 71 | 2.0856 | 1.6939 | 2.3263 | 0.8122 | 812.2 | 0.13508 | 77 | 17.1812 | 13.8865 | 2.349 | 0.80824 | 808.24 | 0.157
[8 empty] | 90 | 3.4801 | 2.7829 | 2.3982 | 0.79966 | 799.66 | 0.13365 |  | 74 | 3.0221 | 2.4486 | 2.3376 | 0.81022 | 810.22 | 0.13397 |  | 66 | 2.8801 | 2.3487 | 2.3074 | 0.8155 | 815.5 | 0.13443 | 66 | 2.8801 | 2.3487 | 2.3074 | 0.8155 | 815.5 | 0.13443 | 72 | 2.0532 | 1.6663 | 2.3301 | 0.81154 | 811.54 | 0.135 | 78 | 16.6931 | 13.481 | 2.3528 | 0.80758 | 807.58 | 0.15696
[8 empty] | 91 | 3.4172 | 2.7303 | 2.402 | 0.799 | 799 | 0.13357 |  | 75 | 2.9682 | 2.403 | 2.3414 | 0.80956 | 809.56 | 0.13392 |  | 67 | 2.828 | 2.3044 | 2.3112 | 0.81484 | 814.84 | 0.13437 | 67 | 2.828 | 2.3044 | 2.3112 | 0.81484 | 814.84 | 0.13437 | 73 | 2.0217 | 1.6394 | 2.3338 | 0.81088 | 810.88 | 0.13492 | 79 | 16.2241 | 13.0916 | 2.3566 | 0.80692 | 806.92 | 0.15692
[8 empty] | 92 | 3.356 | 2.6792 | 2.4057 | 0.79834 | 798.34 | 0.1335 |  | 76 | 2.9159 | 2.3586 | 2.3452 | 0.8089 | 808.9 | 0.13386 |  | 68 | 2.7775 | 2.2614 | 2.3149 | 0.81418 | 814.18 | 0.13431 | 68 | 2.7775 | 2.2614 | 2.3149 | 0.81418 | 814.18 | 0.13431 | 74 | 1.9911 | 1.6132 | 2.3376 | 0.81022 | 810.22 | 0.13485 | 80 | 15.7734 | 12.7174 | 2.3603 | 0.80626 | 806.26 | 0.15688
[8 empty] | 93 | 3.2965 | 2.6295 | 2.4095 | 0.79768 | 797.68 | 0.13342 |  | 77 | 2.865 | 2.3156 | 2.349 | 0.80824 | 808.24 | 0.1338 |  | 69 | 2.7284 | 2.2196 | 2.3187 | 0.81352 | 813.52 | 0.13426 | 69 | 2.7284 | 2.2196 | 2.3187 | 0.81352 | 813.52 | 0.13426 | 75 | 1.9611 | 1.5877 | 2.3414 | 0.80956 | 809.56 | 0.13477 | 81 | 15.3399 | 12.3578 | 2.3641 | 0.8056 | 805.6 | 0.15684
[8 empty] | 94 | 3.2387 | 2.5813 | 2.4133 | 0.79702 | 797.02 | 0.13335 |  | 78 | 2.8155 | 2.2737 | 2.3528 | 0.80758 | 807.58 | 0.13375 |  | 70 | 2.6806 | 2.179 | 2.3225 | 0.81286 | 812.86 | 0.1342 | 70 | 2.6806 | 2.179 | 2.3225 | 0.81286 | 812.86 | 0.1342 | 76 | 1.932 | 1.5628 | 2.3452 | 0.8089 | 808.9 | 0.1347 | 82 | 14.923 | 12.0121 | 2.3679 | 0.80494 | 804.94 | 0.1568
[8 empty] | 95 | 3.1824 | 2.5343 | 2.4171 | 0.79636 | 796.36 | 0.13328 |  | 79 | 2.7673 | 2.233 | 2.3566 | 0.80692 | 806.92 | 0.13369 |  | 71 | 2.6342 | 2.1395 | 2.3263 | 0.8122 | 812.2 | 0.13414 | 71 | 2.6342 | 2.1395 | 2.3263 | 0.8122 | 812.2 | 0.13414 | 77 | 1.9035 | 1.5385 | 2.349 | 0.80824 | 808.24 | 0.13462 | 83 | 14.5219 | 11.6797 | 2.3717 | 0.80428 | 804.28 | 0.15676
[8 empty] | 96 | 3.1277 | 2.4887 | 2.4209 | 0.7957 | 795.7 | 0.1332 |  | 80 | 2.7205 | 2.1934 | 2.3603 | 0.80626 | 806.26 | 0.13363 |  | 72 | 2.5891 | 2.1012 | 2.3301 | 0.81154 | 811.54 | 0.13409 | 72 | 2.5891 | 2.1012 | 2.3301 | 0.81154 | 811.54 | 0.13409 | 78 | 1.8758 | 1.5148 | 2.3528 | 0.80758 | 807.58 | 0.13455 | 84 | 14.1357 | 11.3598 | 2.3755 | 0.80362 | 803.62 | 0.15672
[8 empty] | 97 | 3.0744 | 2.4443 | 2.4247 | 0.79504 | 795.04 | 0.13312 |  | 81 | 2.675 | 2.1549 | 2.3641 | 0.8056 | 805.6 | 0.13358 |  | 73 | 2.5452 | 2.0639 | 2.3338 | 0.81088 | 810.88 | 0.13403 | 73 | 2.5452 | 2.0639 | 2.3338 | 0.81088 | 810.88 | 0.13403 | 79 | 1.8487 | 1.4917 | 2.3566 | 0.80692 | 806.92 | 0.13447 | 85 | 13.7639 | 11.0519 | 2.3793 | 0.80296 | 802.96 | 0.15668
[8 empty] | 98 | 3.0226 | 2.4011 | 2.4284 | 0.79438 | 794.38 | 0.13305 |  | 82 | 2.6306 | 2.1175 | 2.3679 | 0.80494 | 804.94 | 0.13352 |  | 74 | 2.5025 | 2.0276 | 2.3376 | 0.81022 | 810.22 | 0.13397 | 74 | 2.5025 | 2.0276 | 2.3376 | 0.81022 | 810.22 | 0.13397 | 80 | 1.8223 | 1.4692 | 2.3603 | 0.80626 | 806.26 | 0.1344 | 86 | 13.4058 | 10.7555 | 2.383 | 0.8023 | 802.3 | 0.15665
[8 empty] | 99 | 2.9721 | 2.359 | 2.4322 | 0.79372 | 793.72 | 0.13297 |  | 83 | 2.5874 | 2.081 | 2.3717 | 0.80428 | 804.28 | 0.13346 |  | 75 | 2.461 | 1.9923 | 2.3414 | 0.80956 | 809.56 | 0.13392 | 75 | 2.461 | 1.9923 | 2.3414 | 0.80956 | 809.56 | 0.13392 | 81 | 1.7965 | 1.4473 | 2.3641 | 0.8056 | 805.6 | 0.13432 | 87 | 13.0607 | 10.47 | 2.3868 | 0.80164 | 801.64 | 0.15661
[8 empty] | 100 | 2.923 | 2.3181 | 2.436 | 0.79306 | 793.06 | 0.1329 |  | 84 | 2.5454 | 2.0455 | 2.3755 | 0.80362 | 803.62 | 0.13341 |  | 76 | 2.4206 | 1.958 | 2.3452 | 0.8089 | 808.9 | 0.13386 | 76 | 2.4206 | 1.958 | 2.3452 | 0.8089 | 808.9 | 0.13386 | 82 | 1.7713 | 1.4258 | 2.3679 | 0.80494 | 804.94 | 0.13425 | 88 | 12.7281 | 10.1949 | 2.3906 | 0.80098 | 800.98 | 0.15657
[8 empty] | 101 | 2.8752 | 2.2783 | 2.4398 | 0.7924 | 792.4 | 0.13282 |  | 85 | 2.5045 | 2.011 | 2.3793 | 0.80296 | 802.96 | 0.13335 |  | 77 | 2.3812 | 1.9246 | 2.349 | 0.80824 | 808.24 | 0.1338 | 77 | 2.3812 | 1.9246 | 2.349 | 0.80824 | 808.24 | 0.1338 | 83 | 1.7468 | 1.4049 | 2.3717 | 0.80428 | 804.28 | 0.13417 | 89 | 12.4074 | 9.9299 | 2.3944 | 0.80032 | 800.32 | 0.15653
[8 empty] | 102 | 2.8285 | 2.2395 | 2.4436 | 0.79174 | 791.74 | 0.13275 |  | 86 | 2.4646 | 1.9773 | 2.383 | 0.8023 | 802.3 | 0.13329 |  | 78 | 2.3429 | 1.8921 | 2.3528 | 0.80758 | 807.58 | 0.13375 | 78 | 2.3429 | 1.8921 | 2.3528 | 0.80758 | 807.58 | 0.13375 | 84 | 1.7228 | 1.3845 | 2.3755 | 0.80362 | 803.62 | 0.1341 | 90 | 12.098 | 9.6743 | 2.3982 | 0.79966 | 799.66 | 0.15649
[8 empty] | 103 | 2.7831 | 2.2017 | 2.4474 | 0.79108 | 791.08 | 0.13267 |  | 87 | 2.4257 | 1.9446 | 2.3868 | 0.80164 | 801.64 | 0.13324 |  | 79 | 2.3056 | 1.8604 | 2.3566 | 0.80692 | 806.92 | 0.13369 | 79 | 2.3056 | 1.8604 | 2.3566 | 0.80692 | 806.92 | 0.13369 | 85 | 1.6994 | 1.3645 | 2.3793 | 0.80296 | 802.96 | 0.13403 | 91 | 11.7996 | 9.4279 | 2.402 | 0.799 | 799 | 0.15645
[8 empty] | 104 | 2.7389 | 2.1649 | 2.4511 | 0.79042 | 790.42 | 0.1326 |  | 88 | 2.3879 | 1.9126 | 2.3906 | 0.80098 | 800.98 | 0.13318 |  | 80 | 2.2692 | 1.8296 | 2.3603 | 0.80626 | 806.26 | 0.13363 | 80 | 2.2692 | 1.8296 | 2.3603 | 0.80626 | 806.26 | 0.13363 | 86 | 1.6765 | 1.345 | 2.383 | 0.8023 | 802.3 | 0.13395 | 92 | 11.5115 | 9.1901 | 2.4057 | 0.79834 | 798.34 | 0.15641
[8 empty] | 105 | 2.6958 | 2.129 | 2.4549 | 0.78976 | 789.76 | 0.13253 |  | 89 | 2.3509 | 1.8815 | 2.3944 | 0.80032 | 800.32 | 0.13312 |  | 81 | 2.2338 | 1.7995 | 2.3641 | 0.8056 | 805.6 | 0.13358 | 81 | 2.2338 | 1.7995 | 2.3641 | 0.8056 | 805.6 | 0.13358 | 87 | 1.6541 | 1.326 | 2.3868 | 0.80164 | 801.64 | 0.13387 | 93 | 11.2335 | 8.9607 | 2.4095 | 0.79768 | 797.68 | 0.15637
[8 empty] | 106 | 2.6537 | 2.094 | 2.4587 | 0.7891 | 789.1 | 0.13245 |  | 90 | 2.315 | 1.8512 | 2.3982 | 0.79966 | 799.66 | 0.13307 |  | 82 | 2.1993 | 1.7703 | 2.3679 | 0.80494 | 804.94 | 0.13352 | 82 | 2.1993 | 1.7703 | 2.3679 | 0.80494 | 804.94 | 0.13352 | 88 | 1.6323 | 1.3074 | 2.3906 | 0.80098 | 800.98 | 0.1338 | 94 | 10.9649 | 8.7392 | 2.4133 | 0.79702 | 797.02 | 0.15633
[8 empty] | 107 | 2.6127 | 2.06 | 2.4625 | 0.78844 | 788.44 | 0.13237 |  | 91 | 2.2799 | 1.8216 | 2.402 | 0.799 | 799 | 0.13301 |  | 83 | 2.1656 | 1.7418 | 2.3717 | 0.80428 | 804.28 | 0.13346 | 83 | 2.1656 | 1.7418 | 2.3717 | 0.80428 | 804.28 | 0.13346 | 89 | 1.6109 | 1.2893 | 2.3944 | 0.80032 | 800.32 | 0.13372 | 95 | 10.7054 | 8.5254 | 2.4171 | 0.79636 | 796.36 | 0.15629
[8 empty] | 108 | 2.5727 | 2.0267 | 2.4663 | 0.78778 | 787.78 | 0.1323 |  | 92 | 2.2457 | 1.7928 | 2.4057 | 0.79834 | 798.34 | 0.13295 |  | 84 | 2.1328 | 1.714 | 2.3755 | 0.80362 | 803.62 | 0.13341 | 84 | 2.1328 | 1.714 | 2.3755 | 0.80362 | 803.62 | 0.13341 | 90 | 1.5901 | 1.2715 | 2.3982 | 0.79966 | 799.66 | 0.13365 | 96 | 10.4547 | 8.3188 | 2.4209 | 0.7957 | 795.7 | 0.15626
[8 empty] | 109 | 2.5337 | 1.9944 | 2.4701 | 0.78712 | 787.12 | 0.13222 |  | 93 | 2.2123 | 1.7647 | 2.4095 | 0.79768 | 797.68 | 0.1329 |  | 85 | 2.1008 | 1.6869 | 2.3793 | 0.80296 | 802.96 | 0.13335 | 85 | 2.1008 | 1.6869 | 2.3793 | 0.80296 | 802.96 | 0.13335 | 91 | 1.5696 | 1.2541 | 2.402 | 0.799 | 799 | 0.13357 | 97 | 10.2124 | 8.1193 | 2.4247 | 0.79504 | 795.04 | 0.15622
[8 empty] | 110 | 2.4957 | 1.9628 | 2.4738 | 0.78646 | 786.46 | 0.13215 |  | 94 | 2.1797 | 1.7373 | 2.4133 | 0.79702 | 797.02 | 0.13284 |  | 86 | 2.0696 | 1.6605 | 2.383 | 0.8023 | 802.3 | 0.13329 | 86 | 2.0696 | 1.6605 | 2.383 | 0.8023 | 802.3 | 0.13329 | 92 | 1.5497 | 1.2372 | 2.4057 | 0.79834 | 798.34 | 0.1335 | 98 | 9.9781 | 7.9264 | 2.4284 | 0.79438 | 794.38 | 0.15618
[8 empty] | 111 | 2.4586 | 1.9319 | 2.4776 | 0.7858 | 785.8 | 0.13207 |  | 95 | 2.1479 | 1.7105 | 2.4171 | 0.79636 | 796.36 | 0.13278 |  | 87 | 2.0392 | 1.6347 | 2.3868 | 0.80164 | 801.64 | 0.13324 | 87 | 2.0392 | 1.6347 | 2.3868 | 0.80164 | 801.64 | 0.13324 | 93 | 1.5302 | 1.2206 | 2.4095 | 0.79768 | 797.68 | 0.13342 | 99 | 9.7515 | 7.74 | 2.4322 | 0.79372 | 793.72 | 0.15614
[8 empty] | 112 | 2.4223 | 1.9019 | 2.4814 | 0.78514 | 785.14 | 0.132 |  | 96 | 2.1169 | 1.6844 | 2.4209 | 0.7957 | 795.7 | 0.13273 |  | 88 | 2.0095 | 1.6096 | 2.3906 | 0.80098 | 800.98 | 0.13318 | 88 | 2.0095 | 1.6096 | 2.3906 | 0.80098 | 800.98 | 0.13318 | 94 | 1.5111 | 1.2044 | 2.4133 | 0.79702 | 797.02 | 0.13335 | 100 | 9.5323 | 7.5597 | 2.436 | 0.79306 | 793.06 | 0.1561
[8 empty] | 113 | 2.3869 | 1.8725 | 2.4852 | 0.78448 | 784.48 | 0.13192 |  | 97 | 2.0866 | 1.659 | 2.4247 | 0.79504 | 795.04 | 0.13267 |  | 89 | 1.9805 | 1.5851 | 2.3944 | 0.80032 | 800.32 | 0.13312 | 89 | 1.9805 | 1.5851 | 2.3944 | 0.80032 | 800.32 | 0.13312 | 95 | 1.4924 | 1.1885 | 2.4171 | 0.79636 | 796.36 | 0.13328 | 101 | 9.3201 | 7.3853 | 2.4398 | 0.7924 | 792.4 | 0.15606
[8 empty] | 114 | 2.3524 | 1.8439 | 2.489 | 0.78382 | 783.82 | 0.13185 |  | 98 | 2.0571 | 1.6341 | 2.4284 | 0.79438 | 794.38 | 0.13261 |  | 90 | 1.9523 | 1.5612 | 2.3982 | 0.79966 | 799.66 | 0.13307 | 90 | 1.9523 | 1.5612 | 2.3982 | 0.79966 | 799.66 | 0.13307 | 96 | 1.4742 | 1.173 | 2.4209 | 0.7957 | 795.7 | 0.1332 | 102 | 9.1147 | 7.2165 | 2.4436 | 0.79174 | 791.74 | 0.15602
[8 empty] | 115 | 2.3187 | 1.8159 | 2.4928 | 0.78316 | 783.16 | 0.13177 |  | 99 | 2.0282 | 1.6098 | 2.4322 | 0.79372 | 793.72 | 0.13256 |  | 91 | 1.9247 | 1.5378 | 2.402 | 0.799 | 799 | 0.13301 | 91 | 1.9247 | 1.5378 | 2.402 | 0.799 | 799 | 0.13301 | 97 | 1.4563 | 1.1578 | 2.4247 | 0.79504 | 795.04 | 0.13312 | 103 | 8.9159 | 7.0532 | 2.4474 | 0.79108 | 791.08 | 0.15598
[8 empty] | 116 | 2.2857 | 1.7886 | 2.4965 | 0.7825 | 782.5 | 0.1317 |  | 100 | 2 | 1.5861 | 2.436 | 0.79306 | 793.06 | 0.1325 |  | 92 | 1.8977 | 1.515 | 2.4057 | 0.79834 | 798.34 | 0.13295 | 92 | 1.8977 | 1.515 | 2.4057 | 0.79834 | 798.34 | 0.13295 | 98 | 1.4388 | 1.143 | 2.4284 | 0.79438 | 794.38 | 0.13305 | 104 | 8.7233 | 6.8951 | 2.4511 | 0.79042 | 790.42 | 0.15594
[8 empty] | 117 | 2.2536 | 1.7619 | 2.5003 | 0.78184 | 781.84 | 0.13162 |  | 101 | 1.9725 | 1.563 | 2.4398 | 0.7924 | 792.4 | 0.13244 |  | 93 | 1.8714 | 1.4928 | 2.4095 | 0.79768 | 797.68 | 0.1329 | 93 | 1.8714 | 1.4928 | 2.4095 | 0.79768 | 797.68 | 0.1329 | 99 | 1.4217 | 1.1284 | 2.4322 | 0.79372 | 793.72 | 0.13297 | 105 | 8.5368 | 6.742 | 2.4549 | 0.78976 | 789.76 | 0.1559
[8 empty] | 118 | 2.2221 | 1.7359 | 2.5041 | 0.78118 | 781.18 | 0.13155 |  | 102 | 1.9455 | 1.5404 | 2.4436 | 0.79174 | 791.74 | 0.13239 |  | 94 | 1.8457 | 1.471 | 2.4133 | 0.79702 | 797.02 | 0.13284 | 94 | 1.8457 | 1.471 | 2.4133 | 0.79702 | 797.02 | 0.13284 | 100 | 1.405 | 1.1142 | 2.436 | 0.79306 | 793.06 | 0.1329 | 106 | 8.356 | 6.5937 | 2.4587 | 0.7891 | 789.1 | 0.15587
[8 empty] | 119 | 2.1914 | 1.7104 | 2.5079 | 0.78052 | 780.52 | 0.13147 |  | 103 | 1.9192 | 1.5183 | 2.4474 | 0.79108 | 791.08 | 0.13233 |  | 95 | 1.8206 | 1.4498 | 2.4171 | 0.79636 | 796.36 | 0.13278 | 95 | 1.8206 | 1.4498 | 2.4171 | 0.79636 | 796.36 | 0.13278 | 101 | 1.3886 | 1.1003 | 2.4398 | 0.7924 | 792.4 | 0.13282 | 107 | 8.1807 | 6.45 | 2.4625 | 0.78844 | 788.44 | 0.15583
[8 empty] | 120 | 2.1614 | 1.6856 | 2.5117 | 0.77986 | 779.86 | 0.1314 |  | 104 | 1.8935 | 1.4967 | 2.4511 | 0.79042 | 790.42 | 0.13227 |  | 96 | 1.796 | 1.4291 | 2.4209 | 0.7957 | 795.7 | 0.13273 | 96 | 1.796 | 1.4291 | 2.4209 | 0.7957 | 795.7 | 0.13273 | 102 | 1.3725 | 1.0867 | 2.4436 | 0.79174 | 791.74 | 0.13275 | 108 | 8.0109 | 6.3108 | 2.4663 | 0.78778 | 787.78 | 0.15579
[8 empty] | 121 | 2.1321 | 1.6613 | 2.5154 | 0.7792 | 779.2 | 0.13132 |  | 105 | 1.8684 | 1.4756 | 2.4549 | 0.78976 | 789.76 | 0.13222 |  | 97 | 1.7721 | 1.4089 | 2.4247 | 0.79504 | 795.04 | 0.13267 | 97 | 1.7721 | 1.4089 | 2.4247 | 0.79504 | 795.04 | 0.13267 | 103 | 1.3568 | 1.0733 | 2.4474 | 0.79108 | 791.08 | 0.13267 | 109 | 7.8461 | 6.1758 | 2.4701 | 0.78712 | 787.12 | 0.15575
[8 empty] | 122 | 2.1034 | 1.6376 | 2.5192 | 0.77854 | 778.54 | 0.13125 |  | 106 | 1.8438 | 1.455 | 2.4587 | 0.7891 | 789.1 | 0.13216 |  | 98 | 1.7486 | 1.3891 | 2.4284 | 0.79438 | 794.38 | 0.13261 | 98 | 1.7486 | 1.3891 | 2.4284 | 0.79438 | 794.38 | 0.13261 | 104 | 1.3413 | 1.0602 | 2.4511 | 0.79042 | 790.42 | 0.1326 | 110 | 7.6863 | 6.045 | 2.4738 | 0.78646 | 786.46 | 0.15571
[8 empty] | 123 | 2.0753 | 1.6143 | 2.523 | 0.77788 | 777.88 | 0.13117 |  | 107 | 1.8198 | 1.4348 | 2.4625 | 0.78844 | 788.44 | 0.1321 |  | 99 | 1.7257 | 1.3697 | 2.4322 | 0.79372 | 793.72 | 0.13256 | 99 | 1.7257 | 1.3697 | 2.4322 | 0.79372 | 793.72 | 0.13256 | 105 | 1.3262 | 1.0474 | 2.4549 | 0.78976 | 789.76 | 0.13253 | 111 | 7.5312 | 5.918 | 2.4776 | 0.7858 | 785.8 | 0.15567
[8 empty] | 124 | 2.0479 | 1.5917 | 2.5268 | 0.77722 | 777.22 | 0.1311 |  | 108 | 1.7963 | 1.4151 | 2.4663 | 0.78778 | 787.78 | 0.13205 |  | 100 | 1.7033 | 1.3508 | 2.436 | 0.79306 | 793.06 | 0.1325 | 100 | 1.7033 | 1.3508 | 2.436 | 0.79306 | 793.06 | 0.1325 | 106 | 1.3115 | 1.0349 | 2.4587 | 0.7891 | 789.1 | 0.13245 | 112 | 7.3807 | 5.7949 | 2.4814 | 0.78514 | 785.14 | 0.15563
[8 empty] | 125 | 2.0211 | 1.5695 | 2.5306 | 0.77656 | 776.56 | 0.13103 |  | 109 | 1.7733 | 1.3958 | 2.4701 | 0.78712 | 787.12 | 0.13199 |  | 101 | 1.6814 | 1.3324 | 2.4398 | 0.7924 | 792.4 | 0.13244 | 101 | 1.6814 | 1.3324 | 2.4398 | 0.7924 | 792.4 | 0.13244 | 107 | 1.297 | 1.0226 | 2.4625 | 0.78844 | 788.44 | 0.13237 | 113 | 7.2347 | 5.6755 | 2.4852 | 0.78448 | 784.48 | 0.15559
[8 empty] | 126 | 1.9948 | 1.5478 | 2.5344 | 0.7759 | 775.9 | 0.13095 |  | 110 | 1.7509 | 1.377 | 2.4738 | 0.78646 | 786.46 | 0.13193 |  | 102 | 1.66 | 1.3143 | 2.4436 | 0.79174 | 791.74 | 0.13239 | 102 | 1.66 | 1.3143 | 2.4436 | 0.79174 | 791.74 | 0.13239 | 108 | 1.2828 | 1.0105 | 2.4663 | 0.78778 | 787.78 | 0.1323 | 114 | 7.0928 | 5.5595 | 2.489 | 0.78382 | 783.82 | 0.15555
[8 empty] | 127 | 1.9691 | 1.5265 | 2.5381 | 0.77524 | 775.24 | 0.13087 |  | 111 | 1.7289 | 1.3585 | 2.4776 | 0.7858 | 785.8 | 0.13188 |  | 103 | 1.639 | 1.2966 | 2.4474 | 0.79108 | 791.08 | 0.13233 | 103 | 1.639 | 1.2966 | 2.4474 | 0.79108 | 791.08 | 0.13233 | 109 | 1.2688 | 0.99873 | 2.4701 | 0.78712 | 787.12 | 0.13222 | 115 | 6.9551 | 5.447 | 2.4928 | 0.78316 | 783.16 | 0.15551
[8 empty] | 128 | 1.944 | 1.5058 | 2.5419 | 0.77458 | 774.58 | 0.1308 |  | 112 | 1.7073 | 1.3405 | 2.4814 | 0.78514 | 785.14 | 0.13182 |  | 104 | 1.6185 | 1.2793 | 2.4511 | 0.79042 | 790.42 | 0.13227 | 104 | 1.6185 | 1.2793 | 2.4511 | 0.79042 | 790.42 | 0.13227 | 110 | 1.2552 | 0.98716 | 2.4738 | 0.78646 | 786.46 | 0.13215 | 116 | 6.8213 | 5.3377 | 2.4965 | 0.7825 | 782.5 | 0.15548
[8 empty] | 129 | 1.9194 | 1.4855 | 2.5457 | 0.77392 | 773.92 | 0.13072 |  | 113 | 1.6863 | 1.3229 | 2.4852 | 0.78448 | 784.48 | 0.13176 |  | 105 | 1.5985 | 1.2624 | 2.4549 | 0.78976 | 789.76 | 0.13222 | 105 | 1.5985 | 1.2624 | 2.4549 | 0.78976 | 789.76 | 0.13222 | 111 | 1.2418 | 0.97582 | 2.4776 | 0.7858 | 785.8 | 0.13207 | 117 | 6.6913 | 5.2315 | 2.5003 | 0.78184 | 781.84 | 0.15544
[8 empty] | 130 | 1.8953 | 1.4656 | 2.5495 | 0.77326 | 773.26 | 0.13065 |  | 114 | 1.6657 | 1.3056 | 2.489 | 0.78382 | 783.82 | 0.13171 |  | 106 | 1.5789 | 1.2459 | 2.4587 | 0.7891 | 789.1 | 0.13216 | 106 | 1.5789 | 1.2459 | 2.4587 | 0.7891 | 789.1 | 0.13216 | 112 | 1.2287 | 0.9647 | 2.4814 | 0.78514 | 785.14 | 0.132 | 118 | 6.565 | 5.1284 | 2.5041 | 0.78118 | 781.18 | 0.1554
[8 empty] | 131 | 1.8718 | 1.4461 | 2.5533 | 0.7726 | 772.6 | 0.13057 |  | 115 | 1.6455 | 1.2887 | 2.4928 | 0.78316 | 783.16 | 0.13165 |  | 107 | 1.5597 | 1.2297 | 2.4625 | 0.78844 | 788.44 | 0.1321 | 107 | 1.5597 | 1.2297 | 2.4625 | 0.78844 | 788.44 | 0.1321 | 113 | 1.2158 | 0.9538 | 2.4852 | 0.78448 | 784.48 | 0.13192 | 119 | 6.4422 | 5.0282 | 2.5079 | 0.78052 | 780.52 | 0.15536
[8 empty] | 132 | 1.8487 | 1.4271 | 2.5571 | 0.77194 | 771.94 | 0.1305 |  | 116 | 1.6257 | 1.2721 | 2.4965 | 0.7825 | 782.5 | 0.13159 |  | 108 | 1.5409 | 1.2139 | 2.4663 | 0.78778 | 787.78 | 0.13205 | 108 | 1.5409 | 1.2139 | 2.4663 | 0.78778 | 787.78 | 0.13205 | 114 | 1.2032 | 0.94311 | 2.489 | 0.78382 | 783.82 | 0.13185 | 120 | 6.3228 | 4.9309 | 2.5117 | 0.77986 | 779.86 | 0.15532
[8 empty] | 133 | 1.8261 | 1.4084 | 2.5609 | 0.77128 | 771.28 | 0.13042 |  | 117 | 1.6063 | 1.2559 | 2.5003 | 0.78184 | 781.84 | 0.13154 |  | 109 | 1.5224 | 1.1984 | 2.4701 | 0.78712 | 787.12 | 0.13199 | 109 | 1.5224 | 1.1984 | 2.4701 | 0.78712 | 787.12 | 0.13199 | 115 | 1.1908 | 0.93262 | 2.4928 | 0.78316 | 783.16 | 0.13177 | 121 | 6.2066 | 4.8362 | 2.5154 | 0.7792 | 779.2 | 0.15528
[8 empty] | 134 | 1.804 | 1.3902 | 2.5646 | 0.77062 | 770.62 | 0.13035 |  | 118 | 1.5874 | 1.24 | 2.5041 | 0.78118 | 781.18 | 0.13148 |  | 110 | 1.5044 | 1.1832 | 2.4738 | 0.78646 | 786.46 | 0.13193 | 110 | 1.5044 | 1.1832 | 2.4738 | 0.78646 | 786.46 | 0.13193 | 116 | 1.1787 | 0.92234 | 2.4965 | 0.7825 | 782.5 | 0.1317 | 122 | 6.0937 | 4.7442 | 2.5192 | 0.77854 | 778.54 | 0.15524
[8 empty] | 135 | 1.7823 | 1.3723 | 2.5684 | 0.76996 | 769.96 | 0.13027 |  | 119 | 1.5688 | 1.2245 | 2.5079 | 0.78052 | 780.52 | 0.13142 |  | 111 | 1.4868 | 1.1683 | 2.4776 | 0.7858 | 785.8 | 0.13188 | 111 | 1.4868 | 1.1683 | 2.4776 | 0.7858 | 785.8 | 0.13188 | 117 | 1.1668 | 0.91225 | 2.5003 | 0.78184 | 781.84 | 0.13162 | 123 | 5.9838 | 4.6547 | 2.523 | 0.77788 | 777.88 | 0.1552
[8 empty] | 136 | 1.7611 | 1.3548 | 2.5722 | 0.7693 | 769.3 | 0.1302 |  | 120 | 1.5506 | 1.2093 | 2.5117 | 0.77986 | 779.86 | 0.13137 |  | 112 | 1.4695 | 1.1538 | 2.4814 | 0.78514 | 785.14 | 0.13182 | 112 | 1.4695 | 1.1538 | 2.4814 | 0.78514 | 785.14 | 0.13182 | 118 | 1.1551 | 0.90236 | 2.5041 | 0.78118 | 781.18 | 0.13155 | 124 | 5.8769 | 4.5676 | 2.5268 | 0.77722 | 777.22 | 0.15516
[8 empty] | 137 | 1.7403 | 1.3377 | 2.576 | 0.76864 | 768.64 | 0.13012 |  | 121 | 1.5328 | 1.1944 | 2.5154 | 0.7792 | 779.2 | 0.13131 |  | 113 | 1.4526 | 1.1395 | 2.4852 | 0.78448 | 784.48 | 0.13176 | 113 | 1.4526 | 1.1395 | 2.4852 | 0.78448 | 784.48 | 0.13176 | 119 | 1.1437 | 0.89265 | 2.5079 | 0.78052 | 780.52 | 0.13147 | 125 | 5.7728 | 4.4829 | 2.5306 | 0.77656 | 776.56 | 0.15512
[8 empty] | 138 | 1.7199 | 1.3209 | 2.5798 | 0.76798 | 767.98 | 0.13005 |  | 122 | 1.5153 | 1.1797 | 2.5192 | 0.77854 | 778.54 | 0.13125 |  | 114 | 1.436 | 1.1255 | 2.489 | 0.78382 | 783.82 | 0.13171 | 114 | 1.436 | 1.1255 | 2.489 | 0.78382 | 783.82 | 0.13171 | 120 | 1.1324 | 0.88312 | 2.5117 | 0.77986 | 779.86 | 0.1314 | 126 | 5.6715 | 4.4005 | 2.5344 | 0.7759 | 775.9 | 0.15509
[8 empty] | 139 | 1.6999 | 1.3044 | 2.5835 | 0.76732 | 767.32 | 0.12997 |  | 123 | 1.4982 | 1.1654 | 2.523 | 0.77788 | 777.88 | 0.1312 |  | 115 | 1.4197 | 1.1119 | 2.4928 | 0.78316 | 783.16 | 0.13165 | 115 | 1.4197 | 1.1119 | 2.4928 | 0.78316 | 783.16 | 0.13165 | 121 | 1.1214 | 0.87376 | 2.5154 | 0.7792 | 779.2 | 0.13132 | 127 | 5.5729 | 4.3203 | 2.5381 | 0.77524 | 775.24 | 0.15505
[8 empty] | 140 | 1.6804 | 1.2883 | 2.5873 | 0.76666 | 766.66 | 0.1299 |  | 124 | 1.4814 | 1.1514 | 2.5268 | 0.77722 | 777.22 | 0.13114 |  | 116 | 1.4038 | 1.0985 | 2.4965 | 0.7825 | 782.5 | 0.13159 | 116 | 1.4038 | 1.0985 | 2.4965 | 0.7825 | 782.5 | 0.13159 | 122 | 1.1105 | 0.86458 | 2.5192 | 0.77854 | 778.54 | 0.13125 | 128 | 5.4768 | 4.2422 | 2.5419 | 0.77458 | 774.58 | 0.15501
[8 empty] | 141 | 1.6612 | 1.2725 | 2.5911 | 0.766 | 766 | 0.12982 |  | 125 | 1.465 | 1.1376 | 2.5306 | 0.77656 | 776.56 | 0.13108 |  | 117 | 1.3882 | 1.0853 | 2.5003 | 0.78184 | 781.84 | 0.13154 | 117 | 1.3882 | 1.0853 | 2.5003 | 0.78184 | 781.84 | 0.13154 | 123 | 1.0999 | 0.85557 | 2.523 | 0.77788 | 777.88 | 0.13117 | 129 | 5.3832 | 4.1662 | 2.5457 | 0.77392 | 773.92 | 0.15497
[8 empty] | 142 | 1.6424 | 1.257 | 2.5949 | 0.76534 | 765.34 | 0.12975 |  | 126 | 1.4489 | 1.1242 | 2.5344 | 0.7759 | 775.9 | 0.13103 |  | 118 | 1.3729 | 1.0725 | 2.5041 | 0.78118 | 781.18 | 0.13148 | 118 | 1.3729 | 1.0725 | 2.5041 | 0.78118 | 781.18 | 0.13148 | 124 | 1.0894 | 0.84673 | 2.5268 | 0.77722 | 777.22 | 0.1311 | 130 | 5.292 | 4.0921 | 2.5495 | 0.77326 | 773.26 | 0.15493
[8 empty] | 143 | 1.6239 | 1.2418 | 2.5987 | 0.76468 | 764.68 | 0.12967 |  | 127 | 1.433 | 1.111 | 2.5381 | 0.77524 | 775.24 | 0.13097 |  | 119 | 1.3579 | 1.0598 | 2.5079 | 0.78052 | 780.52 | 0.13142 | 119 | 1.3579 | 1.0598 | 2.5079 | 0.78052 | 780.52 | 0.13142 | 125 | 1.0792 | 0.83804 | 2.5306 | 0.77656 | 776.56 | 0.13103 | 131 | 5.2032 | 4.02 | 2.5533 | 0.7726 | 772.6 | 0.15489
[8 empty] | 144 | 1.6058 | 1.2269 | 2.6025 | 0.76402 | 764.02 | 0.1296 |  | 128 | 1.4175 | 1.098 | 2.5419 | 0.77458 | 774.58 | 0.13091 |  | 120 | 1.3432 | 1.0475 | 2.5117 | 0.77986 | 779.86 | 0.13137 | 120 | 1.3432 | 1.0475 | 2.5117 | 0.77986 | 779.86 | 0.13137 | 126 | 1.0691 | 0.82951 | 2.5344 | 0.7759 | 775.9 | 0.13095 | 132 | 5.1166 | 3.9497 | 2.5571 | 0.77194 | 771.94 | 0.15485
[8 empty] | 145 | 1.5881 | 1.2123 | 2.6063 | 0.76336 | 763.36 | 0.12953 |  | 129 | 1.4023 | 1.0853 | 2.5457 | 0.77392 | 773.92 | 0.13086 |  | 121 | 1.3287 | 1.0354 | 2.5154 | 0.7792 | 779.2 | 0.13131 | 121 | 1.3287 | 1.0354 | 2.5154 | 0.7792 | 779.2 | 0.13131 | 127 | 1.0592 | 0.82113 | 2.5381 | 0.77524 | 775.24 | 0.13087 | 133 | 5.0322 | 3.8813 | 2.5609 | 0.77128 | 771.28 | 0.15481
[8 empty] | 146 | 1.5707 | 1.198 | 2.61 | 0.7627 | 762.7 | 0.12945 |  | 130 | 1.3874 | 1.0728 | 2.5495 | 0.77326 | 773.26 | 0.1308 |  | 122 | 1.3146 | 1.0235 | 2.5192 | 0.77854 | 778.54 | 0.13125 | 122 | 1.3146 | 1.0235 | 2.5192 | 0.77854 | 778.54 | 0.13125 | 128 | 1.0495 | 0.81291 | 2.5419 | 0.77458 | 774.58 | 0.1308 | 134 | 4.9499 | 3.8145 | 2.5646 | 0.77062 | 770.62 | 0.15477
[8 empty] | 147 | 1.5536 | 1.1839 | 2.6138 | 0.76204 | 762.04 | 0.12937 |  | 131 | 1.3728 | 1.0606 | 2.5533 | 0.7726 | 772.6 | 0.13074 |  | 123 | 1.3007 | 1.0118 | 2.523 | 0.77788 | 777.88 | 0.1312 | 123 | 1.3007 | 1.0118 | 2.523 | 0.77788 | 777.88 | 0.1312 | 129 | 1.0399 | 0.80483 | 2.5457 | 0.77392 | 773.92 | 0.13072 | 135 | 4.8697 | 3.7495 | 2.5684 | 0.76996 | 769.96 | 0.15473
[8 empty] | 148 | 1.5369 | 1.1701 | 2.6176 | 0.76138 | 761.38 | 0.1293 |  | 132 | 1.3584 | 1.0486 | 2.5571 | 0.77194 | 771.94 | 0.13069 |  | 124 | 1.2871 | 1.0004 | 2.5268 | 0.77722 | 777.22 | 0.13114 | 124 | 1.2871 | 1.0004 | 2.5268 | 0.77722 | 777.22 | 0.13114 | 130 | 1.0306 | 0.79689 | 2.5495 | 0.77326 | 773.26 | 0.13065 | 136 | 4.7914 | 3.686 | 2.5722 | 0.7693 | 769.3 | 0.1547
[8 empty] | 149 | 1.5204 | 1.1566 | 2.6214 | 0.76072 | 760.72 | 0.12922 |  | 133 | 1.3443 | 1.0368 | 2.5609 | 0.77128 | 771.28 | 0.13063 |  | 125 | 1.2738 | 0.98917 | 2.5306 | 0.77656 | 776.56 | 0.13108 | 125 | 1.2738 | 0.98917 | 2.5306 | 0.77656 | 776.56 | 0.13108 | 131 | 1.0213 | 0.78909 | 2.5533 | 0.7726 | 772.6 | 0.13057 | 137 | 4.7151 | 3.6242 | 2.576 | 0.76864 | 768.64 | 0.15466
[8 empty] | 150 | 1.5043 | 1.1434 | 2.6252 | 0.76006 | 760.06 | 0.12915 |  | 134 | 1.3305 | 1.0253 | 2.5646 | 0.77062 | 770.62 | 0.13057 |  | 126 | 1.2607 | 0.97817 | 2.5344 | 0.7759 | 775.9 | 0.13103 | 126 | 1.2607 | 0.97817 | 2.5344 | 0.7759 | 775.9 | 0.13103 | 132 | 1.0123 | 0.78142 | 2.5571 | 0.77194 | 771.94 | 0.1305 | 138 | 4.6406 | 3.5639 | 2.5798 | 0.76798 | 767.98 | 0.15462
[8 empty] | 151 | 1.4885 | 1.1304 | 2.629 | 0.7594 | 759.4 | 0.12907 |  | 135 | 1.3169 | 1.014 | 2.5684 | 0.76996 | 769.96 | 0.13052 |  | 127 | 1.2478 | 0.96738 | 2.5381 | 0.77524 | 775.24 | 0.13097 | 127 | 1.2478 | 0.96738 | 2.5381 | 0.77524 | 775.24 | 0.13097 | 133 | 1.0034 | 0.77389 | 2.5609 | 0.77128 | 771.28 | 0.13042 | 139 | 4.5679 | 3.505 | 2.5835 | 0.76732 | 767.32 | 0.15458
[8 empty] | 152 | 1.473 | 1.1176 | 2.6327 | 0.75874 | 758.74 | 0.129 |  | 136 | 1.3036 | 1.0029 | 2.5722 | 0.7693 | 769.3 | 0.13046 |  | 128 | 1.2352 | 0.95679 | 2.5419 | 0.77458 | 774.58 | 0.13091 | 128 | 1.2352 | 0.95679 | 2.5419 | 0.77458 | 774.58 | 0.13091 | 134 | 0.99464 | 0.76649 | 2.5646 | 0.77062 | 770.62 | 0.13035 | 140 | 4.4969 | 3.4476 | 2.5873 | 0.76666 | 766.66 | 0.15454
[8 empty] | 153 | 1.4577 | 1.1051 | 2.6365 | 0.75808 | 758.08 | 0.12892 |  | 137 | 1.2905 | 0.99195 | 2.576 | 0.76864 | 768.64 | 0.1304 |  | 129 | 1.2229 | 0.9464 | 2.5457 | 0.77392 | 773.92 | 0.13086 | 129 | 1.2229 | 0.9464 | 2.5457 | 0.77392 | 773.92 | 0.13086 | 135 | 0.98605 | 0.75922 | 2.5684 | 0.76996 | 769.96 | 0.13027 | 141 | 4.4276 | 3.3916 | 2.5911 | 0.766 | 766 | 0.1545
[8 empty] | 154 | 1.4428 | 1.0928 | 2.6403 | 0.75742 | 757.42 | 0.12885 |  | 138 | 1.2777 | 0.98124 | 2.5798 | 0.76798 | 767.98 | 0.13035 |  | 130 | 1.2107 | 0.9362 | 2.5495 | 0.77326 | 773.26 | 0.1308 | 130 | 1.2107 | 0.9362 | 2.5495 | 0.77326 | 773.26 | 0.1308 | 136 | 0.9776 | 0.75207 | 2.5722 | 0.7693 | 769.3 | 0.1302 | 142 | 4.36 | 3.3369 | 2.5949 | 0.76534 | 765.34 | 0.15446
[8 empty] | 155 | 1.4281 | 1.0807 | 2.6441 | 0.75676 | 756.76 | 0.12877 |  | 139 | 1.2651 | 0.97073 | 2.5835 | 0.76732 | 767.32 | 0.13029 |  | 131 | 1.1988 | 0.92619 | 2.5533 | 0.7726 | 772.6 | 0.13074 | 131 | 1.1988 | 0.92619 | 2.5533 | 0.7726 | 772.6 | 0.13074 | 137 | 0.96929 | 0.74504 | 2.576 | 0.76864 | 768.64 | 0.13012 | 143 | 4.294 | 3.2835 | 2.5987 | 0.76468 | 764.68 | 0.15442
[8 empty] | 156 | 1.4136 | 1.0689 | 2.6479 | 0.7561 | 756.1 | 0.1287 |  | 140 | 1.2527 | 0.9604 | 2.5873 | 0.76666 | 766.66 | 0.13023 |  | 132 | 1.1871 | 0.91636 | 2.5571 | 0.77194 | 771.94 | 0.13069 | 132 | 1.1871 | 0.91636 | 2.5571 | 0.77194 | 771.94 | 0.13069 | 138 | 0.96113 | 0.73813 | 2.5798 | 0.76798 | 767.98 | 0.13005 | 144 | 4.2295 | 3.2314 | 2.6025 | 0.76402 | 764.02 | 0.15438
[8 empty] | 157 | 1.3995 | 1.0572 | 2.6517 | 0.75544 | 755.44 | 0.12862 |  | 141 | 1.2406 | 0.95027 | 2.5911 | 0.766 | 766 | 0.13018 |  | 133 | 1.1756 | 0.90671 | 2.5609 | 0.77128 | 771.28 | 0.13063 | 133 | 1.1756 | 0.90671 | 2.5609 | 0.77128 | 771.28 | 0.13063 | 139 | 0.9531 | 0.73133 | 2.5835 | 0.76732 | 767.32 | 0.12997 | 145 | 4.1665 | 3.1805 | 2.6063 | 0.76336 | 763.36 | 0.15434
[8 empty] | 158 | 1.3856 | 1.0458 | 2.6554 | 0.75478 | 754.78 | 0.12855 |  | 142 | 1.2286 | 0.94031 | 2.5949 | 0.76534 | 765.34 | 0.13012 |  | 134 | 1.1643 | 0.89724 | 2.5646 | 0.77062 | 770.62 | 0.13057 | 134 | 1.1643 | 0.89724 | 2.5646 | 0.77062 | 770.62 | 0.13057 | 140 | 0.9452 | 0.72465 | 2.5873 | 0.76666 | 766.66 | 0.1299 | 146 | 4.1049 | 3.1308 | 2.61 | 0.7627 | 762.7 | 0.15431
[8 empty] | 159 | 1.3719 | 1.0346 | 2.6592 | 0.75412 | 754.12 | 0.12847 |  | 143 | 1.2169 | 0.93053 | 2.5987 | 0.76468 | 764.68 | 0.13006 |  | 135 | 1.1532 | 0.88793 | 2.5684 | 0.76996 | 769.96 | 0.13052 | 135 | 1.1532 | 0.88793 | 2.5684 | 0.76996 | 769.96 | 0.13052 | 141 | 0.93744 | 0.71808 | 2.5911 | 0.766 | 766 | 0.12982 | 147 | 4.0447 | 3.0823 | 2.6138 | 0.76204 | 762.04 | 0.15427
[8 empty] | 160 | 1.3585 | 1.0235 | 2.663 | 0.75346 | 753.46 | 0.1284 |  | 144 | 1.2054 | 0.92093 | 2.6025 | 0.76402 | 764.02 | 0.13001 |  | 136 | 1.1423 | 0.8788 | 2.5722 | 0.7693 | 769.3 | 0.13046 | 136 | 1.1423 | 0.8788 | 2.5722 | 0.7693 | 769.3 | 0.13046 | 142 | 0.9298 | 0.71162 | 2.5949 | 0.76534 | 765.34 | 0.12975 | 148 | 3.986 | 3.0348 | 2.6176 | 0.76138 | 761.38 | 0.15423
[8 empty] | 161 | 1.3453 | 1.0127 | 2.6668 | 0.7528 | 752.8 | 0.12832 |  | 145 | 1.1941 | 0.91149 | 2.6063 | 0.76336 | 763.36 | 0.12995 |  | 137 | 1.1316 | 0.86982 | 2.576 | 0.76864 | 768.64 | 0.1304 | 137 | 1.1316 | 0.86982 | 2.576 | 0.76864 | 768.64 | 0.1304 | 143 | 0.92229 | 0.70526 | 2.5987 | 0.76468 | 764.68 | 0.12967 | 149 | 3.9285 | 2.9885 | 2.6214 | 0.76072 | 760.72 | 0.15419
[8 empty] | 162 | 1.3323 | 1.0021 | 2.6706 | 0.75214 | 752.14 | 0.12825 |  | 146 | 1.1829 | 0.90222 | 2.61 | 0.7627 | 762.7 | 0.12989 |  | 138 | 1.1211 | 0.86101 | 2.5798 | 0.76798 | 767.98 | 0.13035 | 138 | 1.1211 | 0.86101 | 2.5798 | 0.76798 | 767.98 | 0.13035 | 144 | 0.91491 | 0.69901 | 2.6025 | 0.76402 | 764.02 | 0.1296 | 150 | 3.8723 | 2.9432 | 2.6252 | 0.76006 | 760.06 | 0.15415
[8 empty] | 163 | 1.3196 | 0.99164 | 2.6744 | 0.75148 | 751.48 | 0.12817 |  | 147 | 1.172 | 0.89311 | 2.6138 | 0.76204 | 762.04 | 0.12984 |  | 139 | 1.1108 | 0.85235 | 2.5835 | 0.76732 | 767.32 | 0.13029 | 139 | 1.1108 | 0.85235 | 2.5835 | 0.76732 | 767.32 | 0.13029 | 145 | 0.90764 | 0.69286 | 2.6063 | 0.76336 | 763.36 | 0.12953 | 151 | 3.8174 | 2.8989 | 2.629 | 0.7594 | 759.4 | 0.15411
[8 empty] | 164 | 1.3071 | 0.98137 | 2.6781 | 0.75082 | 750.82 | 0.1281 |  | 148 | 1.1613 | 0.88416 | 2.6176 | 0.76138 | 761.38 | 0.12978 |  | 140 | 1.1007 | 0.84384 | 2.5873 | 0.76666 | 766.66 | 0.13023 | 140 | 1.1007 | 0.84384 | 2.5873 | 0.76666 | 766.66 | 0.13023 | 146 | 0.90049 | 0.6868 | 2.61 | 0.7627 | 762.7 | 0.12945 | 152 | 3.7637 | 2.8557 | 2.6327 | 0.75874 | 758.74 | 0.15407
[8 empty] | 165 | 1.2948 | 0.97128 | 2.6819 | 0.75016 | 750.16 | 0.12802 |  | 149 | 1.1507 | 0.87537 | 2.6214 | 0.76072 | 760.72 | 0.12972 |  | 141 | 1.0907 | 0.83548 | 2.5911 | 0.766 | 766 | 0.13018 | 141 | 1.0907 | 0.83548 | 2.5911 | 0.766 | 766 | 0.13018 | 147 | 0.89346 | 0.68085 | 2.6138 | 0.76204 | 762.04 | 0.12937 | 153 | 3.7112 | 2.8134 | 2.6365 | 0.75808 | 758.08 | 0.15403
[8 empty] | 166 | 1.2827 | 0.96136 | 2.6857 | 0.7495 | 749.5 | 0.12795 |  | 150 | 1.1403 | 0.86672 | 2.6252 | 0.76006 | 760.06 | 0.12967 |  | 142 | 1.0809 | 0.82726 | 2.5949 | 0.76534 | 765.34 | 0.13012 | 142 | 1.0809 | 0.82726 | 2.5949 | 0.76534 | 765.34 | 0.13012 | 148 | 0.88653 | 0.67499 | 2.6176 | 0.76138 | 761.38 | 0.1293 | 154 | 3.6598 | 2.772 | 2.6403 | 0.75742 | 757.42 | 0.15399
[8 empty] | 167 | 1.2708 | 0.95162 | 2.6895 | 0.74884 | 748.84 | 0.12787 |  | 151 | 1.1301 | 0.85822 | 2.629 | 0.7594 | 759.4 | 0.12961 |  | 143 | 1.0713 | 0.81919 | 2.5987 | 0.76468 | 764.68 | 0.13006 | 143 | 1.0713 | 0.81919 | 2.5987 | 0.76468 | 764.68 | 0.13006 | 149 | 0.87972 | 0.66922 | 2.6214 | 0.76072 | 760.72 | 0.12922 | 155 | 3.6095 | 2.7315 | 2.6441 | 0.75676 | 756.76 | 0.15395
[8 empty] | 168 | 1.2591 | 0.94204 | 2.6933 | 0.74818 | 748.18 | 0.1278 |  | 152 | 1.1201 | 0.84987 | 2.6327 | 0.75874 | 758.74 | 0.12955 |  | 144 | 1.0618 | 0.81125 | 2.6025 | 0.76402 | 764.02 | 0.13001 | 144 | 1.0618 | 0.81125 | 2.6025 | 0.76402 | 764.02 | 0.13001 | 150 | 0.87302 | 0.66355 | 2.6252 | 0.76006 | 760.06 | 0.12915 | 156 | 3.5603 | 2.692 | 2.6479 | 0.7561 | 756.1 | 0.15392
[8 empty] | 169 | 1.2476 | 0.93262 | 2.697 | 0.74752 | 747.52 | 0.12772 |  | 153 | 1.1102 | 0.84166 | 2.6365 | 0.75808 | 758.08 | 0.1295 |  | 145 | 1.0525 | 0.80345 | 2.6063 | 0.76336 | 763.36 | 0.12995 | 145 | 1.0525 | 0.80345 | 2.6063 | 0.76336 | 763.36 | 0.12995 | 151 |  |  | 2.629 | 0.7594 | 759.4 | 0.12907 | 157 | 3.5122 | 2.6532 | 2.6517 | 0.75544 | 755.44 | 0.15388
[8 empty] | 170 | 1.2363 | 0.92336 | 2.7008 | 0.74686 | 746.86 | 0.12765 |  | 154 | 1.1006 | 0.83358 | 2.6403 | 0.75742 | 757.42 | 0.12944 |  | 146 | 1.0434 | 0.79579 | 2.61 | 0.7627 | 762.7 | 0.12989 | 146 | 1.0434 | 0.79579 | 2.61 | 0.7627 | 762.7 | 0.12989 | 152 |  |  | 2.6327 | 0.75874 | 758.74 | 0.129 | 158 | 3.4651 | 2.6154 | 2.6554 | 0.75478 | 754.78 | 0.15384
[8 empty] | 171 | 1.2252 | 0.91426 | 2.7046 | 0.7462 | 746.2 | 0.12757 |  | 155 | 1.091 | 0.82564 | 2.6441 | 0.75676 | 756.76 | 0.12938 |  | 147 | 1.0344 | 0.78825 | 2.6138 | 0.76204 | 762.04 | 0.12984 | 147 | 1.0344 | 0.78825 | 2.6138 | 0.76204 | 762.04 | 0.12984 | 153 |  |  | 2.6365 | 0.75808 | 758.08 | 0.12892 | 159 | 3.419 | 2.5783 | 2.6592 | 0.75412 | 754.12 | 0.1538
[8 empty] | 172 | 1.2143 | 0.90531 | 2.7084 | 0.74554 | 745.54 | 0.1275 |  | 156 | 1.0816 | 0.81783 | 2.6479 | 0.7561 | 756.1 | 0.12933 |  | 148 | 1.0256 | 0.78083 | 2.6176 | 0.76138 | 761.38 | 0.12978 | 148 | 1.0256 | 0.78083 | 2.6176 | 0.76138 | 761.38 | 0.12978 | 154 |  |  | 2.6403 | 0.75742 | 757.42 | 0.12885 | 160 | 3.3738 | 2.542 | 2.663 | 0.75346 | 753.46 | 0.15376
[8 empty] | 173 | 1.2036 | 0.89651 | 2.7122 | 0.74488 | 744.88 | 0.12742 |  | 157 | 1.0724 | 0.81015 | 2.6517 | 0.75544 | 755.44 | 0.12927 |  | 149 | 1.0169 | 0.77354 | 2.6214 | 0.76072 | 760.72 | 0.12972 | 149 | 1.0169 | 0.77354 | 2.6214 | 0.76072 | 760.72 | 0.12972 | 155 |  |  | 2.6441 | 0.75676 | 756.76 | 0.12877 | 161 | 3.3296 | 2.5065 | 2.6668 | 0.7528 | 752.8 | 0.15372
[8 empty] | 174 | 1.193 | 0.88785 | 2.716 | 0.74422 | 744.22 | 0.12735 |  | 158 | 1.0634 | 0.8026 | 2.6554 | 0.75478 | 754.78 | 0.12921 |  | 150 | 1.0083 | 0.76638 | 2.6252 | 0.76006 | 760.06 | 0.12967 | 150 | 1.0083 | 0.76638 | 2.6252 | 0.76006 | 760.06 | 0.12967 | 156 |  |  | 2.6479 | 0.7561 | 756.1 | 0.1287 | 162 | 3.2863 | 2.4718 | 2.6706 | 0.75214 | 752.14 | 0.15368
[8 empty] | 175 | 1.1826 | 0.87933 | 2.7197 | 0.74356 | 743.56 | 0.12727 |  | 159 | 1.0544 | 0.79517 | 2.6592 | 0.75412 | 754.12 | 0.12916 |  | 151 | 0.9999 | 0.75932 | 2.629 | 0.7594 | 759.4 | 0.12961 | 151 | 0.9999 | 0.75932 | 2.629 | 0.7594 | 759.4 | 0.12961 | 157 |  |  | 2.6517 | 0.75544 | 755.44 | 0.12862 | 163 | 3.2439 | 2.4377 | 2.6744 | 0.75148 | 751.48 | 0.15364
[8 empty] | 176 | 1.1724 | 0.87096 | 2.7235 | 0.7429 | 742.9 | 0.1272 |  | 160 | 1.0457 | 0.78786 | 2.663 | 0.75346 | 753.46 | 0.1291 |  | 152 | 0.99163 | 0.75239 | 2.6327 | 0.75874 | 758.74 | 0.12955 | 152 | 0.99163 | 0.75239 | 2.6327 | 0.75874 | 758.74 | 0.12955 | 158 |  |  | 2.6554 | 0.75478 | 754.78 | 0.12855 | 164 | 3.2024 | 2.4044 | 2.6781 | 0.75082 | 750.82 | 0.1536
[8 empty] | 177 | 1.1623 | 0.86272 | 2.7273 | 0.74224 | 742.24 | 0.12712 |  | 161 | 1.037 | 0.78067 | 2.6668 | 0.7528 | 752.8 | 0.12904 |  | 153 | 0.98349 | 0.74557 | 2.6365 | 0.75808 | 758.08 | 0.1295 | 153 | 0.98349 | 0.74557 | 2.6365 | 0.75808 | 758.08 | 0.1295 | 159 |  |  | 2.6592 | 0.75412 | 754.12 | 0.12847 | 165 | 3.1617 | 2.3718 | 2.6819 | 0.75016 | 750.16 | 0.15356
[8 empty] | 178 | 1.1524 | 0.85461 | 2.7311 | 0.74158 | 741.58 | 0.12705 |  | 162 | 1.0285 | 0.77359 | 2.6706 | 0.75214 | 752.14 | 0.12899 |  | 154 | 0.97549 | 0.73886 | 2.6403 | 0.75742 | 757.42 | 0.12944 | 154 | 0.97549 | 0.73886 | 2.6403 | 0.75742 | 757.42 | 0.12944 | 160 |  |  | 2.663 | 0.75346 | 753.46 | 0.1284 | 166 | 3.1218 | 2.3398 | 2.6857 | 0.7495 | 749.5 | 0.15353
[8 empty] | 179 | 1.1427 | 0.84663 | 2.7349 | 0.74092 | 740.92 | 0.12697 |  | 163 | 1.0202 | 0.76663 | 2.6744 | 0.75148 | 751.48 | 0.12893 |  | 155 | 0.96762 | 0.73225 | 2.6441 | 0.75676 | 756.76 | 0.12938 | 155 | 0.96762 | 0.73225 | 2.6441 | 0.75676 | 756.76 | 0.12938 | 161 |  |  | 2.6668 | 0.7528 | 752.8 | 0.12832 | 167 | 3.0828 | 2.3085 | 2.6895 | 0.74884 | 748.84 | 0.15349
[8 empty] | 180 | 1.1331 | 0.83878 | 2.7387 | 0.74026 | 740.26 | 0.1269 |  | 164 | 1.0119 | 0.75977 | 2.6781 | 0.75082 | 750.82 | 0.12887 |  | 156 | 0.95987 | 0.72576 | 2.6479 | 0.7561 | 756.1 | 0.12933 | 156 | 0.95987 | 0.72576 | 2.6479 | 0.7561 | 756.1 | 0.12933 | 162 |  |  | 2.6706 | 0.75214 | 752.14 | 0.12825 | 168 | 3.0445 | 2.2778 | 2.6933 | 0.74818 | 748.18 | 0.15345
[8 empty] | 181 | 1.1237 | 0.83106 | 2.7424 | 0.7396 | 739.6 | 0.12682 |  | 165 | 1.0038 | 0.75303 | 2.6819 | 0.75016 | 750.16 | 0.12882 |  | 157 | 0.95224 | 0.71936 | 2.6517 | 0.75544 | 755.44 | 0.12927 | 157 | 0.95224 | 0.71936 | 2.6517 | 0.75544 | 755.44 | 0.12927 | 163 |  |  | 2.6744 | 0.75148 | 751.48 | 0.12817 | 169 | 3.007 | 2.2478 | 2.697 | 0.74752 | 747.52 | 0.15341
[8 empty] | 182 | 1.1144 | 0.82346 | 2.7462 | 0.73894 | 738.94 | 0.12675 |  | 166 |  |  | 2.6857 | 0.7495 | 749.5 | 0.12876 |  | 158 | 0.94474 | 0.71307 | 2.6554 | 0.75478 | 754.78 | 0.12921 | 158 | 0.94474 | 0.71307 | 2.6554 | 0.75478 | 754.78 | 0.12921 | 164 |  |  | 2.6781 | 0.75082 | 750.82 | 0.1281 | 170 | 2.9702 | 2.2183 | 2.7008 | 0.74686 | 746.86 | 0.15337
[8 empty] | 183 | 1.1052 | 0.81597 | 2.75 | 0.73828 | 738.28 | 0.12667 |  | 167 |  |  | 2.6895 | 0.74884 | 748.84 | 0.1287 |  | 159 | 0.93735 | 0.70688 | 2.6592 | 0.75412 | 754.12 | 0.12916 | 159 | 0.93735 | 0.70688 | 2.6592 | 0.75412 | 754.12 | 0.12916 | 165 |  |  | 2.6819 | 0.75016 | 750.16 | 0.12802 | 171 | 2.9341 | 2.1895 | 2.7046 | 0.7462 | 746.2 | 0.15333
[8 empty] | 184 | 1.0962 | 0.80861 | 2.7538 | 0.73762 | 737.62 | 0.1266 |  | 168 |  |  | 2.6933 | 0.74818 | 748.18 | 0.12865 |  | 160 | 0.93008 | 0.70078 | 2.663 | 0.75346 | 753.46 | 0.1291 | 160 | 0.93008 | 0.70078 | 2.663 | 0.75346 | 753.46 | 0.1291 | 166 |  |  | 2.6857 | 0.7495 | 749.5 | 0.12795 | 172 | 2.8988 | 2.1612 | 2.7084 | 0.74554 | 745.54 | 0.15329
[8 empty] | 185 | 1.0874 | 0.80136 | 2.7576 | 0.73696 | 736.96 | 0.12652 |  | 169 |  |  | 2.697 | 0.74752 | 747.52 | 0.12859 |  | 161 | 0.92293 | 0.69478 | 2.6668 | 0.7528 | 752.8 | 0.12904 | 161 | 0.92293 | 0.69478 | 2.6668 | 0.7528 | 752.8 | 0.12904 | 167 |  |  | 2.6895 | 0.74884 | 748.84 | 0.12787 | 173 | 2.8641 | 2.1334 | 2.7122 | 0.74488 | 744.88 | 0.15325
[8 empty] | 186 | 1.0787 | 0.79422 | 2.7614 | 0.7363 | 736.3 | 0.12645 |  | 170 |  |  | 2.7008 | 0.74686 | 746.86 | 0.12853 |  | 162 | 0.91589 | 0.68887 | 2.6706 | 0.75214 | 752.14 | 0.12899 | 162 | 0.91589 | 0.68887 | 2.6706 | 0.75214 | 752.14 | 0.12899 | 168 |  |  | 2.6933 | 0.74818 | 748.18 | 0.1278 | 174 | 2.8301 | 2.1062 | 2.716 | 0.74422 | 744.22 | 0.15321
[8 empty] | 187 | 1.0701 | 0.78719 | 2.7651 | 0.73564 | 735.64 | 0.12637 |  | 171 |  |  | 2.7046 | 0.7462 | 746.2 | 0.12848 |  | 163 | 0.90895 | 0.68306 | 2.6744 | 0.75148 | 751.48 | 0.12893 | 163 | 0.90895 | 0.68306 | 2.6744 | 0.75148 | 751.48 | 0.12893 | 169 |  |  | 2.697 | 0.74752 | 747.52 | 0.12772 | 175 | 2.7968 | 2.0796 | 2.7197 | 0.74356 | 743.56 | 0.15317
[8 empty] | 188 | 1.0616 | 0.78027 | 2.7689 | 0.73498 | 734.98 | 0.1263 |  | 172 |  |  | 2.7084 | 0.74554 | 745.54 | 0.12842 |  | 164 | 0.90213 | 0.67733 | 2.6781 | 0.75082 | 750.82 | 0.12887 | 164 | 0.90213 | 0.67733 | 2.6781 | 0.75082 | 750.82 | 0.12887 | 170 |  |  | 2.7008 | 0.74686 | 746.86 | 0.12765 | 176 | 2.764 | 2.0534 | 2.7235 | 0.7429 | 742.9 | 0.15314
[8 empty] | 189 | 1.0533 | 0.77346 | 2.7727 | 0.73432 | 734.32 | 0.12622 |  | 173 |  |  | 2.7122 | 0.74488 | 744.88 | 0.12836 |  | 165 | 0.8954 | 0.6717 | 2.6819 | 0.75016 | 750.16 | 0.12882 | 165 | 0.8954 | 0.6717 | 2.6819 | 0.75016 | 750.16 | 0.12882 | 171 |  |  | 2.7046 | 0.7462 | 746.2 | 0.12757 | 177 | 2.732 | 2.0278 | 2.7273 | 0.74224 | 742.24 | 0.1531
[8 empty] | 190 | 1.0451 | 0.76675 | 2.7765 | 0.73366 | 733.66 | 0.12615 |  | 174 |  |  | 2.716 | 0.74422 | 744.22 | 0.12831 |  | 166 | 0.88878 | 0.66614 | 2.6857 | 0.7495 | 749.5 | 0.12876 | 166 | 0.88878 | 0.66614 | 2.6857 | 0.7495 | 749.5 | 0.12876 | 172 |  |  | 2.7084 | 0.74554 | 745.54 | 0.1275 | 178 | 2.7005 | 2.0026 | 2.7311 | 0.74158 | 741.58 | 0.15306
[8 empty] | 191 | 1.037 | 0.76014 | 2.7803 | 0.733 | 733 | 0.12607 |  | 175 |  |  | 2.7197 | 0.74356 | 743.56 | 0.12825 |  | 167 | 0.88227 | 0.66068 | 2.6895 | 0.74884 | 748.84 | 0.1287 | 167 | 0.88227 | 0.66068 | 2.6895 | 0.74884 | 748.84 | 0.1287 | 173 |  |  | 2.7122 | 0.74488 | 744.88 | 0.12742 | 179 | 2.6696 | 1.9779 | 2.7349 | 0.74092 | 740.92 | 0.15302
[8 empty] | 192 | 1.0291 | 0.75363 | 2.7841 | 0.73234 | 732.34 | 0.126 |  | 176 |  |  | 2.7235 | 0.7429 | 742.9 | 0.12819 |  | 168 | 0.87585 | 0.65529 | 2.6933 | 0.74818 | 748.18 | 0.12865 | 168 | 0.87585 | 0.65529 | 2.6933 | 0.74818 | 748.18 | 0.12865 | 174 |  |  | 2.716 | 0.74422 | 744.22 | 0.12735 | 180 | 2.6392 | 1.9537 | 2.7387 | 0.74026 | 740.26 | 0.15298
[8 empty] | 193 | 1.0212 | 0.74721 | 2.7878 | 0.73168 | 731.68 | 0.12592 |  | 177 |  |  | 2.7273 | 0.74224 | 742.24 | 0.12814 |  | 169 | 0.86952 | 0.64999 | 2.697 | 0.74752 | 747.52 | 0.12859 | 169 | 0.86952 | 0.64999 | 2.697 | 0.74752 | 747.52 | 0.12859 | 175 |  |  | 2.7197 | 0.74356 | 743.56 | 0.12727 | 181 | 2.6095 | 1.93 | 2.7424 | 0.7396 | 739.6 | 0.15294
[8 empty] | 194 | 1.0135 | 0.7409 | 2.7916 | 0.73102 | 731.02 | 0.12585 |  | 178 |  |  | 2.7311 | 0.74158 | 741.58 | 0.12808 |  | 170 | 0.8633 | 0.64476 | 2.7008 | 0.74686 | 746.86 | 0.12853 | 170 | 0.8633 | 0.64476 | 2.7008 | 0.74686 | 746.86 | 0.12853 | 176 |  |  | 2.7235 | 0.7429 | 742.9 | 0.1272 | 182 | 2.5802 | 1.9066 | 2.7462 | 0.73894 | 738.94 | 0.1529
[8 empty] | 195 | 1.0059 | 0.73467 | 2.7954 | 0.73036 | 730.36 | 0.12577 |  | 179 |  |  | 2.7349 | 0.74092 | 740.92 | 0.12802 |  | 171 | 0.85716 | 0.63961 | 2.7046 | 0.7462 | 746.2 | 0.12848 | 171 | 0.85716 | 0.63961 | 2.7046 | 0.7462 | 746.2 | 0.12848 | 177 |  |  | 2.7273 | 0.74224 | 742.24 | 0.12712 | 183 | 2.5516 | 1.8838 | 2.75 | 0.73828 | 738.28 | 0.15286
[8 empty] | 196 | 0.99841 | 0.72854 | 2.7992 | 0.7297 | 729.7 | 0.1257 |  | 180 |  |  | 2.7387 | 0.74026 | 740.26 | 0.12797 |  | 172 | 0.85112 | 0.63454 | 2.7084 | 0.74554 | 745.54 | 0.12842 | 172 | 0.85112 | 0.63454 | 2.7084 | 0.74554 | 745.54 | 0.12842 | 178 |  |  | 2.7311 | 0.74158 | 741.58 | 0.12705 | 184 | 2.5234 | 1.8613 | 2.7538 | 0.73762 | 737.62 | 0.15282
[8 empty] | 197 | 0.99103 | 0.7225 | 2.803 | 0.72904 | 729.04 | 0.12562 |  | 181 |  |  | 2.7424 | 0.7396 | 739.6 | 0.12791 |  | 173 | 0.84516 | 0.62954 | 2.7122 | 0.74488 | 744.88 | 0.12836 | 173 | 0.84516 | 0.62954 | 2.7122 | 0.74488 | 744.88 | 0.12836 | 179 |  |  | 2.7349 | 0.74092 | 740.92 | 0.12697 | 185 | 2.4957 | 1.8393 | 2.7576 | 0.73696 | 736.96 | 0.15278
[8 empty] | 198 | 0.98375 | 0.71655 | 2.8068 | 0.72838 | 728.38 | 0.12555 |  | 182 |  |  | 2.7462 | 0.73894 | 738.94 | 0.12785 |  | 174 | 0.8393 | 0.62462 | 2.716 | 0.74422 | 744.22 | 0.12831 | 174 | 0.8393 | 0.62462 | 2.716 | 0.74422 | 744.22 | 0.12831 | 180 |  |  | 2.7387 | 0.74026 | 740.26 | 0.1269 | 186 | 2.4686 | 1.8176 | 2.7614 | 0.7363 | 736.3 | 0.15275
[8 empty] | 199 | 0.97658 | 0.71068 | 2.8106 | 0.72772 | 727.72 | 0.12547 |  | 183 |  |  | 2.75 | 0.73828 | 738.28 | 0.1278 |  | 175 | 0.83352 | 0.61977 | 2.7197 | 0.74356 | 743.56 | 0.12825 | 175 | 0.83352 | 0.61977 | 2.7197 | 0.74356 | 743.56 | 0.12825 | 181 |  |  | 2.7424 | 0.7396 | 739.6 | 0.12682 | 187 | 2.4419 | 1.7964 | 2.7651 | 0.73564 | 735.64 | 0.15271
[8 empty] | 200 | 0.96952 | 0.7049 | 2.8143 | 0.72706 | 727.06 | 0.1254 |  | 184 |  |  | 2.7538 | 0.73762 | 737.62 | 0.12774 |  | 176 |  |  | 2.7235 | 0.7429 | 742.9 | 0.12819 | 176 |  |  | 2.7235 | 0.7429 | 742.9 | 0.12819 | 182 |  |  | 2.7462 | 0.73894 | 738.94 | 0.12675 | 188 | 2.4157 | 1.7755 | 2.7689 | 0.73498 | 734.98 | 0.15267
[16 empty] | 185 |  |  | 2.7576 | 0.73696 | 736.96 | 0.12768 |  | 177 |  |  | 2.7273 | 0.74224 | 742.24 | 0.12814 | 177 |  |  | 2.7273 | 0.74224 | 742.24 | 0.12814 | 183 |  |  | 2.75 | 0.73828 | 738.28 | 0.12667 | 189 | 2.39 | 1.755 | 2.7727 | 0.73432 | 734.32 | 0.15263
[16 empty] | 186 |  |  | 2.7614 | 0.7363 | 736.3 | 0.12763 |  | 178 |  |  | 2.7311 | 0.74158 | 741.58 | 0.12808 | 178 |  |  | 2.7311 | 0.74158 | 741.58 | 0.12808 | 184 |  |  | 2.7538 | 0.73762 | 737.62 | 0.1266 | 190 | 2.3647 | 1.7349 | 2.7765 | 0.73366 | 733.66 | 0.15259
[16 empty] | 187 |  |  | 2.7651 | 0.73564 | 735.64 | 0.12757 |  | 179 |  |  | 2.7349 | 0.74092 | 740.92 | 0.12802 | 179 |  |  | 2.7349 | 0.74092 | 740.92 | 0.12802 | 185 |  |  | 2.7576 | 0.73696 | 736.96 | 0.12652 | 191 | 2.3398 | 1.7151 | 2.7803 | 0.733 | 733 | 0.15255
[16 empty] | 188 |  |  | 2.7689 | 0.73498 | 734.98 | 0.12751 |  | 180 |  |  | 2.7387 | 0.74026 | 740.26 | 0.12797 | 180 |  |  | 2.7387 | 0.74026 | 740.26 | 0.12797 | 186 |  |  | 2.7614 | 0.7363 | 736.3 | 0.12645 | 192 | 2.3154 | 1.6957 | 2.7841 | 0.73234 | 732.34 | 0.15251
[16 empty] | 189 |  |  | 2.7727 | 0.73432 | 734.32 | 0.12746 |  | 181 |  |  | 2.7424 | 0.7396 | 739.6 | 0.12791 | 181 |  |  | 2.7424 | 0.7396 | 739.6 | 0.12791 | 187 |  |  | 2.7651 | 0.73564 | 735.64 | 0.12637 | 193 | 2.2914 | 1.6766 | 2.7878 | 0.73168 | 731.68 | 0.15247
[16 empty] | 190 |  |  | 2.7765 | 0.73366 | 733.66 | 0.1274 |  | 182 |  |  | 2.7462 | 0.73894 | 738.94 | 0.12785 | 182 |  |  | 2.7462 | 0.73894 | 738.94 | 0.12785 | 188 |  |  | 2.7689 | 0.73498 | 734.98 | 0.1263 | 194 | 2.2679 | 1.6579 | 2.7916 | 0.73102 | 731.02 | 0.15243
[16 empty] | 191 |  |  | 2.7803 | 0.733 | 733 | 0.12734 |  | 183 |  |  | 2.75 | 0.73828 | 738.28 | 0.1278 | 183 |  |  | 2.75 | 0.73828 | 738.28 | 0.1278 | 189 |  |  | 2.7727 | 0.73432 | 734.32 | 0.12622 | 195 | 2.2447 | 1.6394 | 2.7954 | 0.73036 | 730.36 | 0.15239
[16 empty] | 192 |  |  | 2.7841 | 0.73234 | 732.34 | 0.12729 |  | 184 |  |  | 2.7538 | 0.73762 | 737.62 | 0.12774 | 184 |  |  | 2.7538 | 0.73762 | 737.62 | 0.12774 | 190 |  |  | 2.7765 | 0.73366 | 733.66 | 0.12615 | 196 | 2.2219 | 1.6213 | 2.7992 | 0.7297 | 729.7 | 0.15236
[16 empty] | 193 |  |  | 2.7878 | 0.73168 | 731.68 | 0.12723 |  | 185 |  |  | 2.7576 | 0.73696 | 736.96 | 0.12768 | 185 |  |  | 2.7576 | 0.73696 | 736.96 | 0.12768 | 191 |  |  | 2.7803 | 0.733 | 733 | 0.12607 | 197 | 2.1995 | 1.6035 | 2.803 | 0.72904 | 729.04 | 0.15232
[16 empty] | 194 |  |  | 2.7916 | 0.73102 | 731.02 | 0.12717 |  | 186 |  |  | 2.7614 | 0.7363 | 736.3 | 0.12763 | 186 |  |  | 2.7614 | 0.7363 | 736.3 | 0.12763 | 192 |  |  | 2.7841 | 0.73234 | 732.34 | 0.126 | 198 | 2.1775 | 1.5861 | 2.8068 | 0.72838 | 728.38 | 0.15228
[16 empty] | 195 |  |  | 2.7954 | 0.73036 | 730.36 | 0.12712 |  | 187 |  |  | 2.7651 | 0.73564 | 735.64 | 0.12757 | 187 |  |  | 2.7651 | 0.73564 | 735.64 | 0.12757 | 193 |  |  | 2.7878 | 0.73168 | 731.68 | 0.12592 | 199 | 2.1559 | 1.5689 | 2.8106 | 0.72772 | 727.72 | 0.15224
[16 empty] | 196 |  |  | 2.7992 | 0.7297 | 729.7 | 0.12706 |  | 188 |  |  | 2.7689 | 0.73498 | 734.98 | 0.12751 | 188 |  |  | 2.7689 | 0.73498 | 734.98 | 0.12751 | 194 |  |  | 2.7916 | 0.73102 | 731.02 | 0.12585 | 200 | 2.1346 | 1.552 | 2.8143 | 0.72706 | 727.06 | 0.1522
[16 empty] | 197 |  |  | 2.803 | 0.72904 | 729.04 | 0.127 |  | 189 |  |  | 2.7727 | 0.73432 | 734.32 | 0.12746 | 189 |  |  | 2.7727 | 0.73432 | 734.32 | 0.12746 | 195 |  |  | 2.7954 | 0.73036 | 730.36 | 0.12577
[16 empty] | 198 |  |  | 2.8068 | 0.72838 | 728.38 | 0.12695 |  | 190 |  |  | 2.7765 | 0.73366 | 733.66 | 0.1274 | 190 |  |  | 2.7765 | 0.73366 | 733.66 | 0.1274 | 196 |  |  | 2.7992 | 0.7297 | 729.7 | 0.1257
[16 empty] | 199 |  |  | 2.8106 | 0.72772 | 727.72 | 0.12689 |  | 191 |  |  | 2.7803 | 0.733 | 733 | 0.12734 | 191 |  |  | 2.7803 | 0.733 | 733 | 0.12734 | 197 |  |  | 2.803 | 0.72904 | 729.04 | 0.12562
[16 empty] | 200 |  |  | 2.8143 | 0.72706 | 727.06 | 0.12683 |  | 192 |  |  | 2.7841 | 0.73234 | 732.34 | 0.12729 | 192 |  |  | 2.7841 | 0.73234 | 732.34 | 0.12729 | 198 |  |  | 2.8068 | 0.72838 | 728.38 | 0.12555
[24 empty] | 193 |  |  | 2.7878 | 0.73168 | 731.68 | 0.12723 | 193 |  |  | 2.7878 | 0.73168 | 731.68 | 0.12723 | 199 |  |  | 2.8106 | 0.72772 | 727.72 | 0.12547
[24 empty] | 194 |  |  | 2.7916 | 0.73102 | 731.02 | 0.12717 | 194 |  |  | 2.7916 | 0.73102 | 731.02 | 0.12717 | 200 |  |  | 2.8143 | 0.72706 | 727.06 | 0.1254
[24 empty] | 195 |  |  | 2.7954 | 0.73036 | 730.36 | 0.12712 | 195 |  |  | 2.7954 | 0.73036 | 730.36 | 0.12712
[24 empty] | 196 |  |  | 2.7992 | 0.7297 | 729.7 | 0.12706 | 196 |  |  | 2.7992 | 0.7297 | 729.7 | 0.12706
[24 empty] | 197 |  |  | 2.803 | 0.72904 | 729.04 | 0.127 | 197 |  |  | 2.803 | 0.72904 | 729.04 | 0.127
[24 empty] | 198 |  |  | 2.8068 | 0.72838 | 728.38 | 0.12695 | 198 |  |  | 2.8068 | 0.72838 | 728.38 | 0.12695
[24 empty] | 199 |  |  | 2.8106 | 0.72772 | 727.72 | 0.12689 | 199 |  |  | 2.8106 | 0.72772 | 727.72 | 0.12689
[24 empty] | 200 |  |  | 2.8143 | 0.72706 | 727.06 | 0.12683 | 200 |  |  | 2.8143 | 0.72706 | 727.06 | 0.12683
#REF!
See www.engineeredfluids.com for detailed product information, or contact us at info@engineeredfluids.com
CoolFluids®, and each of the individual CoolFluid product names are trademarks of Engineered Fluids, / ChemFoundry, Inc.
© 2017-2019 Engineered Fluids / ChemFoundry, Inc. All Rights Reserved